## Chassis PSL Left
PSL Chassis |  | Left Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V (routed through relay 1) | violet | L | EK1101 | 0 | 24V | P | R/11 | 12
0V | gray | L | EK1101 | 0 | 0V | P | TBLOCK | –V
24V (routed through relay 1) | violet | L | EK1101 | 0 | + | P | R/11 | 12
0V | gray | L | EK1101 | 0 | – | P | TBLOCK | –V
24V (routed through relay 2) | violet | L | EK1101 | 10 | 24V | P | R/11 | 22
0V | gray | L | EK1101 | 10 | 0V | P | TBLOCK | –V
24V (routed through relay 2) | violet | L | EK1101 | 10 | + | P | R/11 | 22
0V | gray | L | EK1101 | 10 | – | P | TBLOCK | –V
24V | violet | L | CU1521 | 20 | 24V | P | TBLOCK | +V
0V | gray | L | CU1521 | 20 | 0V | P | TBLOCK | –V
24V (routed through relay 1) | violet | R | EL2612 | 11 | 12 | P | 9 | P7
0V | gray |  | TBLOCK |  | 0V | P | 9 | P8
24V (routed through relay 2) | violet | R | EL2612 | 11 | 22 | P | 10 | P7
0V | gray |  | TBLOCK |  | 0V | P | 10 | P8
24V (routed through relay 2) | violet | R | EL2612 | 11 | 22 | P | 11 | P7
0V | gray |  | TBLOCK |  | 0V | P | 11 | P8
24V (routed through relay 1) | violet | R | EL2612 | 11 | 12 | P | 12 | P7
0V | gray |  | TBLOCK |  | 0V | P | 12 | P8
Media Converter
Input | fiber/MM | L | CU1521 | 20 | X1 | Comm. | front | IN
Output | CAT5 | L | CU1521 | 20 | X2 | Comm. | R/0 | X1
Coupler
Output | CAT5 | L | EK1101 | 0
Rotation Stages IO/PSL
Encoder A: A (IO) | brown | L | EL7342 | 1 | A/top | BI | 12 | P4
Encoder A: B (IO) | brown | L | EL7342 | 1 | B/top | BI | 12 | P5
Encoder B: A (Spare) | brown | L | EL7342 | 1 | A/below | BI | 9 | P4
Encoder B: B (Spare) | brown | L | EL7342 | 1 | B/below | BI | 9 | P5
Input A (IO) | brown | L | EL7342 | 1 | I1 | BI | 12 | P3
Input B (Spare) | brown | L | EL7342 | 1 | I2 | BI | 9 | P3
Motor A1(*) (IO) | violet | L | EL7342 | 2 | A1 | P | 12 | PWR/S
Motor A2(*) (IO) | gray | L | EL7342 | 2 | A2 | P | 12 | PWR/P
Motor B1(*) (Spare) | violet | L | EL7342 | 2 | B1 | P | 9 | PWR/S
Motor B2(*) (Spare) | gray | L | EL7342 | 2 | B2 | P | 9 | PWR/P
24V(*) | violet | L | EL7342 | 2 | + | P | L/12 | +
0V(*) | gray | L | EL7342 | 2 | – | P | L/12 | –
Interlock Mon (IO) | brown | L | EL1094 | 3 | I1 | BI | 12 | P9
Interlock Mon (Spare) | brown | L | EL1094 | 3 | I2 | BI | 9 | P9
(empty) | brown | L | EL1094 | 3 | I3 | BI
(empty) | brown | L | EL1094 | 3 | I4 | BI
Coupler
Output | CAT5 | L | EK1101 | 10
Rotation Stages TCS
Encoder A: A (TCSX) | brown | L | EL7342 | 11 | A/top | BI | 10 | P4
Encoder A: B (TCSX) | brown | L | EL7342 | 11 | B/top | BI | 10 | P5
Encoder B: A (TCSY) | brown | L | EL7342 | 11 | A/below | BI | 11 | P4
Encoder B: B (TCSY) | brown | L | EL7342 | 11 | B/below | BI | 11 | P5
Input A (TCSX) | brown | L | EL7342 | 11 | I1 | BI | 10 | P3
Input B (TCSY) | brown | L | EL7342 | 11 | I2 | BI | 11 | P3
Motor A1(*) (TCSX) | violet | L | EL7342 | 12 | A1 | P | 10 | PWR/S
Motor A2(*) (TCSX) | gray | L | EL7342 | 12 | A2 | P | 10 | PWR/P
Motor B1(*) (TCSY) | violet | L | EL7342 | 12 | B1 | P | 11 | PWR/S
Motor B2(*) (TCSY) | gray | L | EL7342 | 12 | B2 | P | 11 | PWR/P
24V(*)(**) | violet | L | EL7342 | 12 | + | P | TBLOCK
0V(*)(**) | gray | L | EL7342 | 12 | – | P | TBLOCK
Interlock Mon (TCSX) | brown | L | EL1094 | 13 | I1 | BI | 10 | P9
Interlock Mon (TCSY) | brown | L | EL1094 | 13 | I2 | BI | 11 | P9
(empty) | brown | L | EL1094 | 13 | I3 | BI
(empty) | brown | L | EL1094 | 13 | I4 | BI
(*) AWG16, twist pairs
(**) Wrap twisted pair through a common mode choke, 10 turns, then connect to terminal block

## Chassis PSL Middle
PSL Chassis |  | Middle Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24VInput | violet | M | EK1100 | 0 | 24V | P | TBLOCK | +V
0VInput | gray | M | EK1100 | 0 | 0V | P | TBLOCK | –V
|  | M | EK1100 | 0 | + | P
Return |  | M | EK1100 | 0 | – | P | 7 | 13
Coupler
Output | CAT5 | M | EK1100 | 0 | X2 | Comm. | front | OUT
P-SAMS
Voltage DC Mon 1 + | green | M | EL3104 | 1 | +I1 | AI | 7 | 1
Voltage DC Mon 1 – | white | M | EL3104 | 1 | –I1 | AI | 7 | 14
Voltage AC Mon 1 + | green | M | EL3104 | 1 | +I2 | AI | 7 | 2
Voltage AC Mon 1 – | white | M | EL3104 | 1 | –I2 | AI | 7 | 15
Voltage DC Mon 2 + | green | M | EL3104 | 1 | +I3 | AI | 7 | 4
Voltage DC Mon 2 – | white | M | EL3104 | 1 | –I3 | AI | 7 | 17
Voltage AC Mon 2 + | green | M | EL3104 | 1 | +I4 | AI | 7 | 5
Voltage AC Mon 2 – | white | M | EL3104 | 1 | –I4 | AI | 7 | 18
Voltage DC Mon 3 + | green | M | EL3104 | 2 | +I1 | AI | 7 | 7
Voltage DC Mon 3 – | white | M | EL3104 | 2 | –I1 | AI | 7 | 20
Voltage AC Mon 3 + | green | M | EL3104 | 2 | +I2 | AI | 7 | 8
Voltage AC Mon 3 – | white | M | EL3104 | 2 | –I2 | AI | 7 | 21
Voltage DC Mon 4 + | green | M | EL3104 | 2 | +I3 | AI | 7 | 10
Voltage DC Mon 4 – | white | M | EL3104 | 2 | –I3 | AI | 7 | 23
Voltage AC Mon 4 + | green | M | EL3104 | 2 | +I4 | AI | 7 | 11
Voltage AC Mon 4 – | white | M | EL3104 | 2 | –I4 | AI | 7 | 24
Voltage DC Ofs 1 + | blue | M | EL4134 | 3 | O1 | AO | 7 | 3
Voltage DC Ofs 1 – | yellow | M | EL4134 | 3 | COM | AO | 7 | 16
Voltage DC Ofs 2 + | blue | M | EL4134 | 3 | O2 | AO | 7 | 6
Voltage DC Ofs 2 – | yellow | M | EL4134 | 3 | COM | AO | 7 | 19
Voltage DC Ofs 3 + | blue | M | EL4134 | 3 | O3 | AO | 7 | 9
Voltage DC Ofs 3 – | yellow | M | EL4134 | 3 | COM | AO | 7 | 22
Voltage DC Ofs 4 + | blue | M | EL4134 | 3 | O4 | AO | 7 | 12
Voltage DC Ofs 4 – | yellow | M | EL4134 | 3 | COM | AO | 7 | 25
Return | black | R | EL9190 | 4 | – | P | 8 | 13
Voltage DC Mon 1 + | green | M | EL3104 | 5 | +I1 | AI | 8 | 1
Voltage DC Mon 1 – | white | M | EL3104 | 5 | –I1 | AI | 8 | 14
Voltage AC Mon 1 + | green | M | EL3104 | 5 | +I2 | AI | 8 | 2
Voltage AC Mon 1 – | white | M | EL3104 | 5 | –I2 | AI | 8 | 15
Voltage DC Mon 2 + | green | M | EL3104 | 5 | +I3 | AI | 8 | 4
Voltage DC Mon 2 – | white | M | EL3104 | 5 | –I3 | AI | 8 | 17
Voltage AC Mon 2 + | green | M | EL3104 | 5 | +I4 | AI | 8 | 5
Voltage AC Mon 2 – | white | M | EL3104 | 5 | –I4 | AI | 8 | 18
Voltage DC Mon 3 + | green | M | EL3104 | 6 | +I1 | AI | 8 | 7
Voltage DC Mon 3 – | white | M | EL3104 | 6 | –I1 | AI | 8 | 20
Voltage AC Mon 3 + | green | M | EL3104 | 6 | +I2 | AI | 8 | 8
Voltage AC Mon 3 – | white | M | EL3104 | 6 | –I2 | AI | 8 | 21
Voltage DC Mon 4 + | green | M | EL3104 | 6 | +I3 | AI | 8 | 10
Voltage DC Mon 4 – | white | M | EL3104 | 6 | –I3 | AI | 8 | 23
Voltage AC Mon 4 + | green | M | EL3104 | 6 | +I4 | AI | 8 | 11
Voltage AC Mon 4 – | white | M | EL3104 | 6 | –I4 | AI | 8 | 24
Voltage DC Ofs 1 + | blue | M | EL4134 | 7 | O1 | AO | 8 | 3
Voltage DC Ofs 1 – | yellow | M | EL4134 | 7 | COM | AO | 8 | 16
Voltage DC Ofs 2 + | blue | M | EL4134 | 7 | O2 | AO | 8 | 6
Voltage DC Ofs 2 – | yellow | M | EL4134 | 7 | COM | AO | 8 | 19
Voltage DC Ofs 3 + | blue | M | EL4134 | 7 | O3 | AO | 8 | 9
Voltage DC Ofs 3 – | yellow | M | EL4134 | 7 | COM | AO | 8 | 22
Voltage DC Ofs 4 + | blue | M | EL4134 | 7 | O4 | AO | 8 | 12
Voltage DC Ofs 4 – | yellow | M | EL4134 | 7 | COM | AO | 8 | 25

## Chassis PSL Right
PSL Chassis |  | Right Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24VInput | violet | R | EK1101 | 0 | 24V | P | TBLOCK | +V
0VInput | gray | R | EK1101 | 0 | 0V | P | TBLOCK | –V
24VInput | violet | R | EK1101 | 0 | + | P | TBLOCK | +V
0VInput | gray | R | EK1101 | 0 | – | P | TBLOCK | –V
24V | violet | R | EL9410 | 12 | 24V | P | TBLOCK | +V
0V | gray | R | EL9410 | 12 | 0V | P | TBLOCK | –V
24V | violet | R | EL9410 | 12 | + | P | TBLOCK | +V
0V | gray | R | EL9410 | 12 | – | P | TBLOCK | –V
24V | violet | R | EL9410 | 17 | 24V | P | TBLOCK | +V
0V | gray | R | EL9410 | 17 | 0V | P | TBLOCK | –V
|  | R | EL9410 | 17 | + | P
|  | R | EL9410 | 17 | – | P | 6A & 6B | 13
Coupler
Output | CAT5 | R | EK1101 | 0 | X2 | Comm. | M/0 | X1
Environmental
H1:PSL-ENV_LASERRM_ACSTEMP(+V)out | violet | R | EL3154 | 1 | 24V | P | 1 | 1
H1:PSL-ENV_LASERRM_ACSTEMP(current)in | green | R | EL3154 | 1 | I1 | AI | 1 | 14
H1:PSL-ENV_LASERRM_ACNTEMP(+V)out | violet | R | EL3154 | 1 | 24V | P | 1 | 2
H1:PSL-ENV_LASERRM_ACNTEMP(current)in | green | R | EL3154 | 1 | I2 | AI | 1 | 15
H1:PSL-ENV_LASERRM_TBLNTEMP(+V)out | violet | R | EL3154 | 1 | 24V | P | 1 | 3
H1:PSL-ENV_LASERRM_TBLNTEMP(current)in | green | R | EL3154 | 1 | I3 | AI | 1 | 16
H1:PSL-ENV_LASERRM_RH(current)in | green | R | EL3154 | 1 | I4 | AI | 1 | 4
H1:PSL-ENV_LASERRM_TBLSTEMP(+V)out | violet | R | EL3154 | 2 | 24V | P | 1 | 5
H1:PSL-ENV_LASERRM_TBLSTEMP(current)in | green | R | EL3154 | 2 | I1 | AI | 1 | 18
H1:PSL-ENV_ANTERM_TEMP(+V)out | violet | R | EL3154 | 2 | 24V | P | 1 | 6
H1:PSL-ENV_ANTERM_TEMP(current)in | green | R | EL3154 | 2 | I2 | AI | 1 | 19
H1:PSL-ENV_ANTERM_RH(current)in | green | R | EL3154 | 2 | I3 | AI | 1 | 7
H1:PSL-ENV_LVEA_TEMP(+V)out | violet | R | EL3154 | 2 | 24V | P | 1 | 8
H1:PSL-ENV_LVEA_TEMP(current)in | green | R | EL3154 | 2 | I4 | Al | 1 | 21
H1:PSL-ENV_LASERRMTOANTERM_DPRES(+V)out | violet | R | EL3154 | 3 | 24v | P | 1 | 9
H1:PSL-ENV_LASERRMTOANTERM_DPRES(current)in | green | R | EL3154 | 3 | I1 | AI | 1 | 22
H1:PSL-ENV_ANTERMTOLVEA_DPRES(+V)out | violet | R | EL3154 | 3 | 24V | P | 1 | 10
H1:PSL-ENV_ANTERMTOLVEA_DPRES(current)in | green | R | EL3154 | 3 | I2 | AI | 1 | 23
H1:PSL-ENV_DIODERM_TEMP(+V)out | violet | R | EL3154 | 3 | 24V | P | 2 | 1
H1:PSL-ENV_DIODERM_TEMP(current)in | green | R | EL3154 | 3 | I3 | AI | 2 | 14
H1:PSL-ENV_DIODERM_RH(current)in | green | R | EL3154 | 3 | I4 | AI | 2 | 2
H1:PSL-ENV_CHILLERRM_TEMP(+V)out | violet | R | EL3154 | 4 | 24V | P | 2 | 3
H1:PSL-ENV_CHILLERRM_TEMP(current)in | green | R | EL3154 | 4 | I1 | AI | 2 | 16
H1:PSL-ENV_CHILLERRM_RH(current)in | green | R | EL3154 | 4 | I2 | AI | 2 | 4
H1:PSL-ENV_DIODERMTOCHILLERRM_DPRES(+V)out | violet | R | EL3154 | 4 | 24V | P | 2 | 5
H1:PSL-ENV_DIODERMTOCHILLERRM_DPRES(current)in | green | R | EL3154 | 4 | I3 | AI | 2 | 18
(Empty) | violet | R | EL3154 | 4 | 24V | P | 2 | 6
(Empty) | green | R | EL3154 | 4 | I4 | AI | 2 | 19
IO PZTs
Return | black | R | EL9190 | 5 | – | P | 3 | 1/8
V-Mon 1 + | green | R | EL3104 | 6 | +I1 | AI | 3 | 1/3
V-Mon 1 – | white | R | EL3104 | 6 | –I1 | AI | R/5 | Return
V-Mon 2 + | green | R | EL3104 | 6 | +I2 | AI | 3 | 1/4
V-Mon 2 – | white | R | EL3104 | 6 | –I2 | AI | R/5 | Return
SGS-Mon X + | green | R | EL3104 | 6 | +I3 | AI | 3 | 1/9
SGS-Mon X – | white | R | EL3104 | 6 | –I3 | AI | R/5 | Return
SGS-Mon Y + | green | R | EL3104 | 6 | +I4 | AI | 3 | 1/10
SGS-Mon Y – | white | R | EL3104 | 6 | –I4 | AI | R/5 | Return
Return | black | R | EL9190 | 7 | – | P | 3 | 2/8
V-Mon 1 + | green | R | EL3104 | 8 | +I1 | AI | 3 | 2/3
V-Mon 1 – | white | R | EL3104 | 8 | –I1 | AI | R/7 | Return
V-Mon 2 + | green | R | EL3104 | 8 | +I2 | AI | 3 | 2/4
V-Mon 2 – | white | R | EL3104 | 8 | –I2 | AI | R/7 | Return
SGS-Mon X + | green | R | EL3104 | 8 | +I3 | AI | 3 | 2/9
SGS-Mon X – | white | R | EL3104 | 8 | –I3 | AI | R/7 | Return
SGS-Mon Y + | green | R | EL3104 | 8 | +I4 | AI | 3 | 2/10
SGS-Mon Y – | white | R | EL3104 | 8 | –I4 | AI | R/7 | Return
Rotation Stage Feed
Output | CAT5 | R | EK2211 | 9 | X1 | Comm. | L/0 | IN
Output | CAT5 | R | EK2211 | 9 | X2 | Comm. | L/10 | IN
Relay 11 | violet | R | EL2612 | 11 | 11 | Contact | TBLOCK | +V
Relay 12 (see page 1) | violet | R | EL2612 | 11 | 12 | Contact | L/0 | 24V
Relay 14 (empty) |  | R | EL2612 | 11 | 14 | Contact
Relay 21 | violet | R | EL2612 | 11 | 21 | Contact | TBLOCK | +V
Relay 22 (see page 1) | violet | R | EL2612 | 11 | 22 | Contact | L/10 | 24V
Relay 24 (empty) |  | R | EL2612 | 11 | 24 | Contact
Picomotor Controller A (**)
0V | gray | R | EL3102 | 13 | COM | P | TBLOCK
Temperature Monitor 1 + | green | R | EL3102 | 13 | +I1 | AI | 4 | 6
Temperature Monitor 1 – | white | R | EL3102 | 13 | –I1 | AI | 4 | 5
Temperature Monitor 2 + | green | R | EL3102 | 13 | +I2 | AI | 4 | 4
Temperature Monitor 2 – | white | R | EL3102 | 13 | –I2 | AI | 4 | 3
Driver Fault 1 | brown | R | EL1014 | 14 | I1 | BI | 4 | 10
Driver Fault 2 | brown | R | EL1014 | 14 | I2 | BI | 4 | 9
Remote ON | brown | R | EL1014 | 14 | I3 | BI | 4 | 8
Power ON | brown | R | EL1014 | 14 | I4 | BI | 4 | 7
Readbacks | IDC | R | EL1872 | 15 | X1 | BI | 4 | P12
24V | violet | R | EL1872 | 15 | 1 | P | TBLOCK
0V | gray | R | EL1872 | 15 | 2 | P | TBLOCK
Controls | IDC | R | EL2872 | 16 | X1 | BO | 4 | P11
24V | violet | R | EL2872 | 16 | 1 | P | TBLOCK
0V | gray | R | EL2872 | 16 | 2 | P | TBLOCK
T-SAMS
Voltage Mon 1A + | green | R | EL3104 | 18 | +I1 | AI | 6A | 4
Voltage Mon 1A – | white | R | EL3104 | 18 | –I1 | AI | 6A | 17
Current Mon 1A + | green | R | EL3104 | 18 | +I2 | AI | 6A | 3
Current Mon 1A – | white | R | EL3104 | 18 | –I2 | AI | 6A | 16
Voltage Mon 2A + | green | R | EL3104 | 18 | +I3 | AI | 6A | 2
Voltage Mon 2A – | white | R | EL3104 | 18 | –I3 | AI | 6A | 15
Current Mon 2A + | green | R | EL3104 | 18 | +I4 | AI | 6A | 1
Current Mon 2A – | white | R | EL3104 | 18 | –I4 | AI | 6A | 14
Voltage Mon 1B + | green | R | EL3104 | 19 | +I1 | AI | 6B | 4
Voltage Mon 1B – | white | R | EL3104 | 19 | –I1 | AI | 6B | 17
Current Mon 1B + | green | R | EL3104 | 19 | +I2 | AI | 6B | 3
Current Mon 1B – | white | R | EL3104 | 19 | –I2 | AI | 6B | 16
Voltage Mon 2B + | green | R | EL3104 | 19 | +I3 | AI | 6B | 2
Voltage Mon 2B – | white | R | EL3104 | 19 | –I3 | AI | 6B | 15
Current Mon 2B + | green | R | EL3104 | 19 | +I4 | AI | 6B | 1
Current Mon 2B – | white | R | EL3104 | 19 | –I4 | AI | 6B | 14
Temperature Supply 1A + | red | R | EL3692 | 20 | +R1 | AI | 6A | 10
Temperature Supply 1A – | black | R | EL3692 | 20 | –R1 | AI | 6A | 23
Temperature Readback 1A + | green | R | EL3692 | 20 | +RL1 | AI | 6A | 12
Temperature Readback 1A – | white | R | EL3692 | 20 | –RL1 | AI | 6A | 25
Temperature Supply 2A + | red | R | EL3692 | 20 | +R2 | AI | 6A | 9
Temperature Supply 2A – | black | R | EL3692 | 20 | –R2 | AI | 6A | 22
Temperature Readback 2A + | green | R | EL3692 | 20 | +RL2 | AI | 6A | 11
Temperature Readback 2A – | white | R | EL3692 | 20 | –RL2 | AI | 6A | 24
Temperature Supply 1B + | red | R | EL3692 | 21 | +R1 | AI | 6B | 10
Temperature Supply 1B – | black | R | EL3692 | 21 | –R1 | AI | 6B | 23
Temperature Readback 1B + | green | R | EL3692 | 21 | +RL1 | AI | 6B | 12
Temperature Readback 1B – | white | R | EL3692 | 21 | –RL1 | AI | 6B | 25
Temperature Supply 2B + | red | R | EL3692 | 21 | +R2 | AI | 6B | 9
Temperature Supply 2B – | black | R | EL3692 | 21 | –R2 | AI | 6B | 22
Temperature Readback 2B + | green | R | EL3692 | 21 | +RL2 | AI | 6B | 11
Temperature Readback 2B – | white | R | EL3692 | 21 | –RL2 | AI | 6B | 24
Set current/voltage 1A + | blue | R | EL4132 | 22 | O1 | AO | 6A | 6
Set current/voltage 1A – | yellow | R | EL4132 | 22 | COM | AO | 6A | 19
Set current/voltage 1B + | blue | R | EL4132 | 22 | O2 | AO | 6B | 6
Set current/voltage 1B – | yellow | R | EL4132 | 22 | COM | AO | 6B | 19
** Terminal order is out-of sequence between the two picomotor controllers (EL1872 and EL2872 are clustered at the end)