## Copy of CarlsEdit_v12 1
Designator | Termination A | Termination A Connector | Chassis U# | Description | Termination B | Termination B Connector | Chassis U# | Cable Type | Length Feet
CAB_L1: ISC_1 | R1 | DB9M | 18 ; Monitor | D0901781 Mode Cleaner Servo To 32 CH AA Anti Aliasing (LSC_ADC0-7) | C1 | DB9F | 9 ; PORT 7 | DB9 | 149
CAB_L1: ISC_2 | R1 | DB25F | 24 ; Controls | D090605 79.4MHz VCO (PSL) To D1002961 Beckhoff EtherCAT ISC Common (CM Servo, VCO, Delay Line) | C2 | DB25M | 19 ; EtherCAT 1-PORT 5 | DB25 | 147
CAB_L1: ISC_3 | R1 | DB25M | 35 ; Controls | D1000124 24.078MHz RF Distribution Amp To D1100262 RF Amp Concentrator 2-5 | C3 | DB25F | 16 ; PORT 5 | DB25 | 145
CAB_L1: ISC_4 | R1 | DB15M | 20 ; Controls | D1000181 24.078MHz 2-Channel Demodulator To D1100691 LSC Demod Concentrator 1 | R1 | DB15F | 16 ; Demodulator 2B | DB15 | 5
CAB_L1: ISC_5 | R1 | DB37M | 18 ; Controls 1 | D0901781 Mode Cleaner Servo To D1002961 Beckhoff EtherCAT 1-6 (CM Servo, VCO, Delay Line) | C2 | DB37F | 19 ; PORT 6 | DB37 | 147
CAB_L1: ISC_6 | R1 | DB37M | 18 ; Controls 2 | D0901781 Mode Cleaner Servo To D1002961 Beckhoff EtherCAT 1-7 (CM Servo, VCO, Delay Line) | C2 | DB37F | 19 ; PORT 7 | DB37 | 147
CAB_L1: ISC_7 | R1 | DB25F | 21 ; Controls 1 | D0900128 24.078MHz Dual Delay Line To D1002961 Beckhoff EtherCAT 1-3 (CM Servo, VCO, Delay Line) | C2 | DB25M | 19 ; PORT 3 | DB25 | 147
CAB_L1: ISC_8 | R1 | DB9M | 9 ; RF Mon Output Ch 1 & 2 | D0902796 WFS I&Q Demodulator (ASC IMC WFS_A_24MHz) To D1100696 ASC Demod Concentrator 1 | R1 | DB9F | 16 ; Demodulator 1A | DB9 | 14
CAB_L1: ISC_9 | R1 | DB9M | 9 ; RF Mon Output Ch 3 & 4 | D0902796 WFS I&Q Demodulator (ASC IMC WFS_A_24MHz) To D1100696 ASC Demod Concentrator 1 | R1 | DB9F | 16 ; Demodulator 2A | DB9 | 14
CAB_L1: ISC_10 | R1 | DB25M | 9 : I & Q Output | D0902796 WFS I&Q Demodulator (ASC IMC WFS_A_24MHz) To D1002559 ISC Whitening (ASC IMC WFS_A_24MHz) | R1 | DB25F | 11 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_11 | R1 | DB9M | 7 ; RF Mon Output Ch 1 & 2 | D0902796 WFS I&Q Demodulator (ASC IMC WFS_B_24MHz) To D1100696 ASC Demod Concentrator 1 | R1 | DB9F | 16 ; Demodulator 3A | DB9 | 14
CAB_L1: ISC_12 | R1 | DB9M | 7 ; RF Mon Output Ch 3 & 4 | D0902796 WFS I&Q Demodulator (ASC IMC WFS_B_24MHz) To D1100696 ASC Demod Concentrator 1 | R1 | DB9F | 16 ; Demodulator 4A | DB9 | 14
CAB_L1: ISC_13 | R1 | DB25M | 7 : I & Q Output | D0902796 WFS I&Q Demodulator (ASC IMC WFS_B_24MHz) To D1002559 ISC Whitening (ASC IMC WFS_B_24MHz) | R1 | DB25F | 5 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_14 | R1 | DB9M | 11 ; Analog out 0-3 | D1002559 ISC Whitening (ASC IMC WFS_A_24MHz) To 32 CH AA Anti Aliasing (ASC_ADC0) ; PORT 1 | C1 | DB9F | 37 ; PORT 1 | DB9 | 149
CAB_L1: ISC_15 | R1 | DB9M | 11 ; Analog out 4-7 | D1002559 ISC Whitening (ASC IMC WFS_A_24MHz) To 32 CH AA Anti Aliasing (ASC_ADC0) | C1 | DB9F | 37 ; PORT 2 | DB9 | 149
CAB_L1: ISC_16 | R1 | DB9M | 5 ; Analog out 0-3 | D1002559 ISC Whitening (ASC IMC WFS_B_24MHz) To 32 CH AA Anti Aliasing (ASC_ADC0) | C1 | DB9F | 37 ; PORT 3 | DB9 | 149
CAB_L1: ISC_17 | R1 | DB9M | 5 ; Analog out 4-7 | D1002559 ISC Whitening (ASC IMC WFS_B_24MHz) To 32 CH AA Anti Aliasing (ASC_ADC0) | C1 | DB9F | 37 ; PORT 4 | DB9 | 149
CAB_L1: ISC_18 | R1 | DB37M | 11 ; Board 1, From Binary Output Module | D1002559 ISC Whitening (ASC IMC WFS_B_24MHz) To 32 CH AA Anti Aliasing (ASC_ADC0) | C2 | DB37M | 33 ; CHASSIS 1-1 | DB37 | 147
CAB_L1: ISC_19 | R1 | DB37M | 11 ; Board 2, From Binary Output Module | D1002559 ISC Whitening (ASC IMC WFS_A_24MHz) To D1100251 384 Channel Binary Output (BO1) Whitening ; CHASSIS 1-2 | C2 | DB37M | 33 ; CHASSIS 1-2 | DB37 | 147
CAB_L1: ISC_20 | R1 | DB37M | 5 ; Board 1, From Binary Output Module | D1002559 ISC Whitening (ASC IMC WFS_B_24MHz) To D1100251 384 Channel Binary Output (BO1) Whitening ; CHASSIS 2-1 | C2 | DB37M | 33 ; CHASSIS 2-1 | DB37 | 147
CAB_L1: ISC_21 | R1 | DB37M | 5 ; Board 2, From Binary Output Module | D1002559 ISC Whitening (ASC IMC WFS_B_24MHz) To D1100251 384 Channel Binary Output (BO1) Whitening ; CHASSIS 2-2 | C2 | DB37M | 33 ; CHASSIS 2-2 | DB37 | 147
CAB_L1: ISC_22 | R1 | DB9M | 13 ; DC Outputs Head 1 | D1101865 Vertex WFS Interface To 32 CH AA Anti Aliasing (ASC_ADC0) | C1 | DB9F | 37 ; PORT 5 | DB9 | 149
CAB_L1: ISC_23 | R1 | DB9M | 13 ; DC Outputs Head 2 | D1101865 Vertex WFS Interface To 32 CH AA Anti Aliasing (ASC_ADC0) | C1 | DB9F | 37 ; PORT 6 | DB9 | 149
CAB_L1: ISC_24 | IOT2RL | DB15F | IMC_WFS_A FLANGE | IOT2L IMC_WFS_A Flange To D1101906 Vertex WFS Interface | R1 | DB15M | 13 ; HEAD 1 | DB15 | 50
CAB_L1: ISC_25 | IOT2RL | DB15F | IMC_WFS_B FLANGE | IOT2L IMC_WFS_B Flange To D1101906 Vertex WFS Interface | R1 | DB15M | 13 ; HEAD 2 | DB15 | 50
CAB_L1: ISC_26 | IOT2RL | DB9F | IMC_PDH FLANGE | IOT2L IMC_PDH Flange To D1102079 LSC RF PD INTERFACE | R1 | DB9M | 14 ; To LSC Head 1 | DB9 | 50
CAB_L1: ISC_27 | R1 | DB25M | 26-27 ; Controls | D090605 79.4MHz VCO (ALS) Low Noise VCO To D1100681 Beckhoff EtherCAT 3-5 (LSC Demod, VCO, Delay Line, RF Amps) | C2 | DB25F | 11 ; Port 5 | DB25 | 147
CAB_L1: ISC_28 | R1 | DB25M | 32-33 ; Controls | D090605 79.4MHz VCO (ALS DIFF) Low Noise VCO To D1200132 Beckhoff EtherCAT corner 5 | C2 | DB25F | 3; PORT 5 | DB25 | 147
CAB_L1: ISC_29 | R2 | DB25M | 28 ; I & Q Output | D0902796 WFS I&Q Demodulator (LSC POPAIR B 18 & 90,LSC REFLAIR B 27 & 135) To D1002559 Whitening (LSC POPAIR B 18 & 90,LSC REFLAIR B 27 & 135) | R2 | DB25F | 26 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_30 | R2 | DB25M | 30 ; I & Q Output | D0902796 WFS I&Q Demodulator (LSC POPAIR A 9 & 45,LSC REFLAIR A 45) To D1002559 Whitening (LSC POPAIR A 9 & 45,LSC REFLAIR A 45) | R2 | DB25F | 32 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_31 | R2 | DB25M | 24 ; ; I & Q Output | D0902796 WFS I&Q Demodulator (LSC POP, LSC REFL) To D1002559 Whitening (LSC POP, LSC REFL) | R2 | DB25F | 22 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_32 | R2 | DB25M | 18 ; I & Q Output | D0902796 WFS I&Q Demodulator (ASC REFLAIR A 9 MHz) To D1002559 Whitening (ASC REFLAIR A 9 MHz) | R2 | DB25F | 20 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_33 | R2 | DB25M | 16 ; I & Q Output | D0902796 WFS I&Q Demodulator (ASC REFLAIR A 45 MHz) To D1002559 Whitening (ASC REFLAIR A 45 MHz) | R2 | DB25F | 14 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_34 | R2 | DB25M | 10 ; I & Q Output | D0902796 WFS I&Q Demodulator (ASC REFLAIR B 9 MHz) To D1002559 Whitening (ASC REFLAIR B 9 MHz) | R2 | DB25F | 12 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_35 | R2 | DB25M | 8 ; I & Q Output | D0902796 WFS I&Q Demodulator (ASC REFLAIR B 45 MHz) To D1002559 Whitening (ASC REFLAIR B 45 MHz) | R2 | DB25F | 6 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_36 | R2 | DB25M | 4 ; I & Q Output | D0902796 WFS I&Q Demodulator (spare chain for air to vac leapfrog) To D1002559 Whitening (spare chain for air to vac leapfrog) | R2 | DB25F | 2 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_37 | R4 | DB25M | 25 ; To Whitening | D1002481 Dual QPD Transimpedance Amp (Ham 3) To D1002559 Whitening (Ham 3) ISC-ASC_POP | R4 | DB25F | 26 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_38 | R5 | DB25M | 24; To Whitening | D1002481 Dual QPD Amp (ASC OMCR A&B) To D1002559 Whitening/VGA (ASC OMCR A&B) | R5 | DB25F | 22; Analog Signal Input | DB25 | 6
CAB_L1: ISC_39 | R5 | DB25M | 20; To Whitening | D1002481 Dual QPD Amp (ASC AS C) To D1002559 Whitening/VGA (ASC AS C) | R5 | DB25F | 18; Analog Signal Input | DB25 | 6
CAB_L1: ISC_40 | R3 | DB25M | 21; I & Q Outputs | D0902796 WFS I&Q Demodulator (Spare Chain for air to vac leapfrog) To D1002559 ISC Whitening (Spare Chain for air to vac leapfrog) | R3 | DB25F | 23; Analog Singnal Input | DB25 | 6
CAB_L1: ISC_41 | R3 | DB25M | 27; I & Q Outputs | D0902796 WFS I&Q Demodulator (ASC ASAIR A 45MHz) To D1002559 ISC Whitening (ASC ASAIR A 45MHz) | R3 | DB25F | 25; Analog Singnal Input | DB25 | 6
CAB_L1: ISC_42 | R3 | DB25M | 29; I & Q Outputs | D0902796 WFS I&Q Demodulator (ASC ASAIR A 36MHz) To D1002559 ISC Whitening (ASC ASAIR A 36MHz) | R3 | DB25F | 31; Analog Singnal Input | DB25 | 6
CAB_L1: ISC_43 | R3 | DB25M | 14; I & Q Outputs | D0902796 WFS I&Q Demodulator (ASC ASAIR B 45MHz) To D1002559 ISC Whitening (ASC ASAIR B 45MHz) | R3 | DB25F | 12; Analog Singnal Input | DB25 | 6
CAB_L1: ISC_44 | R3 | DB25M | 16; I & Q Outputs | D0902796 WFS I&Q Demodulator (ASC ASAIR B 36MHz) To D1002559 ISC Whitening (ASC ASAIR B 36MHz) | R3 | DB25F | 18; Analog Singnal Input | DB25 | 6
CAB_L1: ISC_45 | R3 | DB25M | 8; I & Q Outputs | D0902796 LSC I&Q Demodulator (LSC ASAIR A 45MHz, LSC ASAIRB 19MHz, LSC ASAIR B 90MHz)To D1002559 ISC Whitening (LSC ASAIR A 45MHz, LSC ASAIRB 19MHz, LSC ASAIR B 90MHz) | R3 | DB25F | 10; Analog Singnal Input | DB25 | 6
CAB_L1: ISC_46 | R1 | DB15M | 29 ; Controls | D1002476 158.8/79.4MHz 2 CH Phase Frequency Discriminator To D1100691 LSC Demod Concentrator 1 | R1 | DB15F | 16 ; Demodulator 1B | DB15 | 5
CAB_L1: ISC_47 | R1 | DB37M | 16 ; Controls | D1100691 LSC Demod Concentrator 1 To D1100681 Beckhoff EtherCAT 3 (LSC Demod, Serial VCO, Delay Line, RF Amps) | C2 | DB37F | 11 ; EtherCAT 3-PORT 1 | DB37 | 147
CAB_L1: ISC_48 | R1 | DB37M | 15 ; Controls A | D1100691 ASC Demod Concentrator 1 To D1101266 Beckhoff EtherCAT 4 (ASC Demod) | C2 | DB37F | 6 ; EtherCAT 4-PORT 1 | DB37 | 147
CAB_L1: ISC_49 | R2 | DB25M | 37 ; Controls | D1000124 9.099/8.684MHz Distribution Amp To D1100262 RF Amp Concentrator 2-6 | C3 | DB25F | 16 ; PORT 6 | DB25 | 143
CAB_L1: ISC_50 | R2 | DB25M | 38 ; Controls | D1000124 45MHz Distribution Amp To D1100262 RF Amp Concentrator 2-7 | C3 | DB25F | 16 ; PORT 7 | DB25 | 143
CAB_L1: ISC_51 | R2 | DB9M | 28 ; RF Mon Output Ch 1 & 2 | D0902796 LSC I&Q Demodulator (LSC POPAIR B 18 & 90,LSC REFLAIR B 27 & 135) To D1100691 LSC Demod Concentrator 3 | R4 | DB9F | 41 ; Demodulator 3 | DB9 | 12
CAB_L1: ISC_52 | R2 | DB9M | 28 ; RF Mon Output Ch 3 & 4 | D0902796 LSC I&Q Demodulator (LSC POPAIR B 18 & 90,LSC REFLAIR B 27 & 135) To D1100691 LSC Demod Concentrator 3 | R4 | DB9F | 41 ; Demodulator 4 | DB9 | 12
CAB_L1: ISC_53 | R2 | DB37M | 26 ; Board 1, From Binary Output Module | D1002559 Whitening (LSC POPAIR B 18 & 90,LSC REFLAIR B 27 & 135) To D1100251 384 Channel Binary Out Whitening (BO1); CHASSIS 3-board 1 | C2 | DB37M | 33 ; CHASSIS 3-1 | DB37 | 145
CAB_L1: ISC_54 | R2 | DB37M | 26 ; Board 2, From Binary Output Module | D1002559 Whitening (LSC POPAIR B 18 & 90,LSC REFLAIR B 27 & 135) To D1100251 384 Channel Binary Out Whitening (BO1); CHASSIS 3-board 2 | C2 | DB37M | 33 ; CHASSIS 3-2 | DB37 | 145
CAB_L1: ISC_55 | R2 | DB37M | 32 ; Board 1, From Binary Output Module | D1002559 (LSC POPAIR A 9 & 45,LSC REFLAIR A 45) To D1100251 384 Channel Binary Out Whitening (BO1); CHASSIS 4-board 1 | C2 | DB37M | 33 ; CHASSIS 4-1 | DB37 | 145
CAB_L1: ISC_56 | R2 | DB37M | 32 ; Board 2, From Binary Output Module | D1002559 (LSC POPAIR A 9 & 45,LSC REFLAIR A 45) To D1100251 384 Channel Binary Out Whitening (BO1); CHASSIS 4-board 2 | C2 | DB37M | 33 ; CHASSIS 4-2 | DB37 | 145
CAB_L1: ISC_57 | R2 | DB9M | 30 ; RF Mon Output Ch 1 & 2 | D0902796 LSC I&Q Demodulator (LSC POPAIR A 9 & 45,LSC REFLAIR A 45) To D1100691 LSC Demod Concentrator 3 | R4 | DB9F | 41 ; Demodulator 1 | DB9 | 12
CAB_L1: ISC_58 | R2 | DB9M | 30 ; RF Mon Output Ch 3 & 4 | D0902796 LSC I&Q Demodulator (LSC POPAIR A 9 & 45,LSC REFLAIR A 45) To D1100691 LSC Demod Concentrator 3 | R4 | DB9F | 41 ; Demodulator 2 | DB9 | 12
CAB_L1: ISC_59 | R2 | DB37M | 22 ; Board 1, From Binary Output Module | D1002559 Whitening (LSC POP, LSC REFL) To D1100251 384 Channel Binary Out Whitening (BO1); CHASSIS 5-1 | C2 | DB37M | 33 ; CHASSIS 5-1 | DB37 | 145
CAB_L1: ISC_60 | R2 | DB37M | 22 ; Board 2, From Binary Output Module | D1002559 Whitening (LSC POP, LSC REFL) To D1100251 384 Channel Binary Out Whitening (BO1); CHASSIS 5-2 | C2 | DB37M | 33 ; CHASSIS 5-2 | DB37 | 145
CAB_L1: ISC_61 | R2 | DB37M | 20 ; Board 1, From Binary Output Module | D1002559 Whitening (ASC REFLAIR A 9 MHz) To D1100251 384 Channel Binary Out Whitening (BO1); CHASSIS 6-1 | C2 | DB37M | 33 ; CHASSIS 6-1 | DB37 | 145
CAB_L1: ISC_62 | R2 | DB37M | 20 ; Board 2, From Binary Output Module | D1002559 Whitening (ASC REFLAIR A 9 MHz) To D1100251 384 Channel Binary Out Whitening (BO1); CHASSIS 6-2 | C2 | DB37M | 33 ; CHASSIS 6-2 | DB37 | 145
CAB_L1: ISC_63 | R2 | DB9M | 26 ; Analog Out 0-3 | D1002559 Whitening (LSC POPAIR B 18 & 90,LSC REFLAIR B 27 & 135) To 32 CH AA Anti Aliasing (LSC_ADC1) | C1 | DB9F | 8 ; PORT 1 | DB9 | 147
CAB_L1: ISC_64 | R2 | DB9M | 26 ; Analog Out 4-7 | D1002559 Whitening (LSC POPAIR B 18 & 90,LSC REFLAIR B 27 & 135) To 32 CH AA Anti Aliasing (LSC_ADC1) | C1 | DB9F | 8 ; PORT 2 | DB9 | 147
CAB_L1: ISC_65 | R2 | DB9M | 32 ; Analog Out 0-3 | D1002559 Whitening (LSC POPAIR A 9 & 45,LSC REFLAIR A 45) To 32 CH AA Anti Aliasing (LSC_ADC1) | C1 | DB9F | 8 ; PORT 5 | DB9 | 147
CAB_L1: ISC_66 | R2 | DB9M | 32 ; Analog Out 4-7 | D1002559 Whitening (LSC POPAIR A 9 & 45,LSC REFLAIR A 45) To 32 CH AA Anti Aliasing (LSC_ADC1) | C1 | DB9F | 8 ; PORT 6 | DB9 | 147
CAB_L1: ISC_67 | R2 | DB15M | 34 ; Controls | D1000181 9.099/8.684MHz 2-Channel Demodulator To D1100691 LSC Demod Concentrator 2 | R4 | DB15F | 42; PORT 2 | DB15 | 12
CAB_L1: ISC_68 | R2 | DB25F | 36; Controls 1 | D0900128 9.099/8.684MHz Dual Delay Line To D1100681 EtherCAT Corner Station 3 | C2 | DB25M | 11; PORT 6 | DB25 | 145
CAB_L1: ISC_69 | R2 | DB9M | 24 ; RF Mon Output Ch 1 & 2 | D0902796 LSC I&Q Demodulator (LSC POP, LSC REFL) To D1100691 LSC Demod Concentrator 2 | R4 | DB9F | 42 ; PORT 3 | DB9 | 12
CAB_L1: ISC_70 | R2 | DB9M | 24 ; RF Mon Output Ch 3 & 4 | D0902796 LSC I&Q Demodulator (LSC POP, LSC REFL) To D1100691 LSC Demod Concentrator 2 | R4 | DB9F | 42 ; PORT 4 | DB9 | 12
CAB_L1: ISC_71 | R2 | DB9M | 18 ; RF Mon Output Ch 1 & 2 | D0902796 ASC I&Q Demodulator (ASC REFLAIR A 9 MHz) To D1100696 ASC Demod Concentrator 2 | R4 | DB9F | 40 ; PORT 1A | DB9 | 12
CAB_L1: ISC_72 | R2 | DB9M | 18 ; RF Mon Output Ch 3 & 4 | D0902796 ASC I&Q Demodulator (ASC REFLAIR A 9 MHz) To D1100696 ASC Demod Concentrator 2 | R4 | DB9F | 40 ; PORT 2A | DB9 | 12
CAB_L1: ISC_73 | R2 | DB9M | 16 ; RF Mon Output Ch 1 & 2 | D0902796 ASC I&Q Demodulator (ASC REFLAIR A 45 MHz) To D1100696 ASC Demod Concentrator 2 | R4 | DB9F | 40 ; PORT 3A | DB9 | 12
CAB_L1: ISC_74 | R2 | DB9M | 16 ; RF Mon Output Ch 3 & 4 | D0902796 ASC I&Q Demodulator (ASC REFLAIR A 45 MHz) To D1100696 ASC Demod Concentrator 2 | R4 | DB9F | 40 ; PORT 4A | DB9 | 12
CAB_L1: ISC_75 | R2 | DB9M | 10 ; RF Mon Output Ch 1 & 2 | D0902796 ASC I&Q Demodulator (ASC REFLAIR B 9 MHz) To D1100696 ASC Demod Concentrator 2 | R4 | DB9F | 40 ; PORT 1B | DB9 | 12
CAB_L1: ISC_76 | R2 | DB9M | 10 ; RF Mon Output Ch 3 & 4 | D0902796 ASC I&Q Demodulator (ASC REFLAIR B 9 MHz) To D1100696 ASC Demod Concentrator 2 | R4 | DB9F | 40 ; PORT 2B | DB9 | 12
CAB_L1: ISC_77 | R2 | DB9M | 8 ; RF Mon Output Ch 1 & 2 | D0902796 ASC I&Q Demodulator (ASC REFLAIR B 45 MHz) To D1100696 ASC Demod Concentrator 2 | R4 | DB9F | 40 ; PORT 3B | DB9 | 12
CAB_L1: ISC_78 | R2 | DB9M | 8 ; RF Mon Output Ch 3 & 4 | D0902796 ASC I&Q Demodulator (ASC REFLAIR B 45 MHz) To D1100696 ASC Demod Concentrator 2 | R4 | DB9F | 40 ; PORT 4B | DB9 | 12
CAB_L1: ISC_79 | R2 | DB9M | 4 ; RF Mon Output Ch 1 & 2 | D0902796 ASC I&Q Demodulator (spare chain for air to vac leapfrog) To D1100696 ASC Demod Concentrator 3 | R4 | DB9F | 39 ; PORT 1A | DB9 | 12
CAB_L1: ISC_80 | R2 | DB9M | 4 ; RF Mon Output Ch 3 & 4 | D0902796 ASC I&Q Demodulator (spare chain for air to vac leapfrog) To D1100696 ASC Demod Concentrator 3 | R4 | DB9F | 39 ; PORT 1B | DB9 | 12
CAB_L1: ISC_81 | R2 | DB37M | 14 ; Board 1, From Binary Output Module | D1002559 Whitening (ASC REFLAIR A 45 MHz) To D1100251 384 Channel Binary Out Whitening (BO2); CHASSIS 1-board 1 | C2 | DB37M | 31 ; CHASSIS 1-1 | DB37 | 145
CAB_L1: ISC_82 | R2 | DB37M | 14 ; Board 2, From Binary Output Module | D1002559 Whitening (ASC REFLAIR A 45 MHz) To D1100251 384 Channel Binary Out Whitening (BO2); CHASSIS 1-board 2 | C2 | DB37M | 31 ; CHASSIS 1-2 | DB37 | 145
CAB_L1: ISC_83 | R2 | DB37M | 12 ; Board 1, From Binary Output Module | D1002559 Whitening (ASC REFLAIR B 9 MHz) To D1100251 384 Channel Binary Out Whitening (BO2); CHASSIS 2-board 1 | C2 | DB37M | 31 ; CHASSIS 2-1 | DB37 | 145
CAB_L1: ISC_84 | R2 | DB37M | 12 ; Board 2, From Binary Output Module | D1002559 Whitening (ASC REFLAIR B 9 MHz) To D1100251 384 Channel Binary Out Whitening (BO2); CHASSIS 2-board 2 | C2 | DB37M | 31 ; CHASSIS 2-2 | DB37 | 145
CAB_L1: ISC_85 | R2 | DB37M | 6 ; Board 1, From Binary Output Module | D1002559 Whitening (ASC REFLAIR B 45 MHz) To D1100251 384 Channel Binary Out (BO2) Whitening ; CHASSIS 3-board 1 | C2 | DB37M | 31 ; CHASSIS 3-1 | DB37 | 145
CAB_L1: ISC_86 | R2 | DB37M | 6 ; Board 2, From Binary Output Module | D1002559 Whitening (ASC REFLAIR B 45 MHz) To D1100251 384 Channel Binary Out (BO2) Whitening ; CHASSIS 3-board 2 | C2 | DB37M | 31 ; CHASSIS 3-2 | DB37 | 145
CAB_L1: ISC_87 | R2 | DB37M | 2 ; Board 1, From Binary Output Module | D1002559 Whitening (spare chain for air to vac leapfrog) To D1100251 384 Channel Binary Out (BO2) Whitening ; CHASSIS 4-board 1 | C2 | DB37M | 31 ; CHASSIS 4-1 | DB37 | 145
CAB_L1: ISC_88 | R2 | DB37M | 2 ; Board 2, From Binary Output Module | D1002559 Whitening (spare chain for air to vac leapfrog) To D1100251 384 Channel Binary Out (BO2) Whitening ; CHASSIS 4-board 2 | C2 | DB37M | 31 ; CHASSIS 4-2 | DB37 | 145
CAB_L1: ISC_89 | R4 | DB37M | 26 ; Board 1, From Binary Output Module | D1002559 Whitening (Ham 3) To D1100251 384 Channel Binary Out (BO2) Whitening ; CHASSIS 5-board 1 | C2 | DB37M | 31 ; CHASSIS 5-1 | DB37 | 142
CAB_L1: ISC_90 | R4 | DB37M | 26 ; Board 2, From Binary Output Module | D1002559 Whitening (Ham 3) To D1100251 384 Channel Binary Out (BO2) Whitening ; CHASSIS 5-board 2 | C2 | DB37M | 31 ; CHASSIS 5-2 | DB37 | 142
CAB_L1: ISC_91 | R5 | DB37M | 22; Board 1, From Binary Output Module | D1002559 Whitening/VGA (ASC OMCR A&B) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 1-1 | C2 | DB37M | 28 ; CHASSIS 1-1 | DB37 | 129
CAB_L1: ISC_92 | R5 | DB37M | 22; Board 2, From Binary Output Module | D1002559 Whitening/VGA (ASC OMCR A&B) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 1-2 | C2 | DB37M | 28 ; CHASSIS 1-2 | DB37 | 129
CAB_L1: ISC_93 | R5 | DB37M | 18; Board 1, From Binary Output Module | D1002559 Whitening/VGA (ASC AS C) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 2-1 | C2 | DB37M | 28 ; CHASSIS 2-1 | DB37 | 129
CAB_L1: ISC_94 | R5 | DB37M | 18; Board 2, From Binary Output Module | D1002559 Whitening/VGA (ASC AS C) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 2-2 | C2 | DB37M | 28 ; CHASSIS 2-2 | DB37 | 129
CAB_L1: ISC_95 | R3 | DB37M | 23; Board 1, From Binary Output Module | D1002559 ISC Whitening (Spare Chain for air to vac leapfrog) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 3-1 | C2 | DB37M | 28 ; CHASSIS 3-1 | DB37 | 126
CAB_L1: ISC_96 | R3 | DB37M | 23; Board 2, From Binary Output Module | D1002559 ISC Whitening (Spare Chain for air to vac leapfrog) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 3-2 | C2 | DB37M | 28 ; CHASSIS 3-2 | DB37 | 126
CAB_L1: ISC_97 | R3 | DB37M | 25; Board 1, From Binary Output Module | D1002559 ISC Whitening (ASC ASAIR A 45MHz) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 4-1 | C2 | DB37M | 28 ; CHASSIS 4-1 | DB37 | 126
CAB_L1: ISC_98 | R3 | DB37M | 25; Board 2, From Binary Output Module | D1002559 ISC Whitening (ASC ASAIR A 45MHz) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 4-2 | C2 | DB37M | 28 ; CHASSIS 4-2 | DB37 | 126
CAB_L1: ISC_99 | R3 | DB37M | 31; Board 1, From Binary Output Module | D1002559 ISC Whitening (ASC ASAIR A 36MHz) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 5-1 | C2 | DB37M | 28 ; CHASSIS 5-1 | DB37 | 126
CAB_L1: ISC_100 | R3 | DB37M | 31; Board 2, From Binary Output Module | D1002559 ISC Whitening (ASC ASAIR A 36MHz) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 5-2 | C2 | DB37M | 28 ; CHASSIS 5-2 | DB37 | 126
CAB_L1: ISC_101 | R3 | DB37M | 12; Board 1, From Binary Output Module | D1002559 ISC Whitening (ASC ASAIR B 45MHz) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 6-1 | C2 | DB37M | 28 ; CHASSIS 6-1 | DB37 | 126
CAB_L1: ISC_102 | R3 | DB37M | 12; Board 2, From Binary Output Module | D1002559 ISC Whitening (ASC ASAIR B 45MHz) To D1100251 384 Channel Binary Out (BO3) Whitening ; CHASSIS 6-2 | C2 | DB37M | 28 ; CHASSIS 6-2 | DB37 | 126
CAB_L1: ISC_103 | R3 | DB37M | 18; Board 1, From Binary Output Module | D1002559 ISC Whitening (ASC ASAIR B 36MHz) To D1100251 384 Channel Binary Out (BO4) Whitening ; CHASSIS 1-1 | C2 | DB37M | 26 ; CHASSIS 1-1 | DB37 | 126
CAB_L1: ISC_104 | R3 | DB37M | 18; Board 2, From Binary Output Module | D1002559 ISC Whitening (ASC ASAIR B 36MHz) To D1100251 384 Channel Binary Out (BO4) Whitening ; CHASSIS 1-2 | C2 | DB37M | 26 ; CHASSIS 1-2 | DB37 | 126
CAB_L1: ISC_105 | R2 | DB9M | 22 ; Analog Out 0-3 | D1002559 Whitening (LSC POP, LSC REFL) To 32 CH AA Anti Aliasing (LSC_ADC1) | C1 | DB9F | 8 ; PORT 7 | DB9 | 147
CAB_L1: ISC_106 | R2 | DB9M | 22 ; Analog Out 4-7 | D1002559 Whitening (LSC POP, LSC REFL) To 32 CH AA Anti Aliasing (LSC_ADC1) | C1 | DB9F | 8 ; PORT 8 | DB9 | 147
CAB_L1: ISC_107 | R2 | DB9M | 20 ; Analog Out 0-3 | D1002559 Whitening (ASC REFLAIR A 9 MHz) To 32 CH AA Anti Aliasing (ASC_ADC2) | C1 | DB9F | 34 ; PORT 1 | DB9 | 147
CAB_L1: ISC_108 | R2 | DB9M | 20 ; Analog Out 4-7 | D1002559 Whitening (ASC REFLAIR A 9 MHz) To 32 CH AA Anti Aliasing (ASC_ADC2) | C1 | DB9F | 34 ; PORT 2 | DB9 | 147
CAB_L1: ISC_109 | R2 | DB9M | 14 ; Analog Out 0-3 | D1002559 Whitening (ASC REFLAIR A 45 MHz) To 32 CH AA Anti Aliasing (ASC_ADC2) | C1 | DB9F | 34 ; PORT 3 | DB9 | 147
CAB_L1: ISC_110 | R2 | DB9M | 14 ; Analog Out 4-7 | D1002559 Whitening (ASC REFLAIR A 45 MHz) To 32 CH AA Anti Aliasing (ASC_ADC2) | C1 | DB9F | 34 ; PORT 4 | DB9 | 147
CAB_L1: ISC_111 | R2 | DB9M | 12 ; Analog Out 0-3 | D1002559 Whitening (ASC REFLAIR B 9 MHz) To 32 CH AA Anti Aliasing (ASC_ADC2) | C1 | DB9F | 34 ; PORT 5 | DB9 | 147
CAB_L1: ISC_112 | R2 | DB9M | 12 ; Analog Out 4-7 | D1002559 Whitening (ASC REFLAIR B 9 MHz) To 32 CH AA Anti Aliasing (ASC_ADC2) | C1 | DB9F | 34 ; PORT 6 | DB9 | 147
CAB_L1: ISC_113 | R2 | DB9M | 6 ; Analog Out 0-3 | D1002559 Whitening (ASC REFLAIR B 45 MHz) To 32 CH AA Anti Aliasing (ASC_ADC2) | C1 | DB9F | 34 ; PORT 7 | DB9 | 147
CAB_L1: ISC_114 | R2 | DB9M | 6 ; Analog Out 4-7 | D1002559 Whitening (ASC REFLAIR B 45 MHz) To 32 CH AA Anti Aliasing (ASC_ADC2) | C1 | DB9F | 34 ; PORT 8 | DB9 | 147
CAB_L1: ISC_115 | R2 | DB9M | 2 ; Analog Out 0-3 | D1002559 Whitening (spare chain for air to vac leapfrog) To 32 CH AA Anti Aliasing (ASC_ADC3) | C1 | DB9F | 33 ; PORT 1 | DB9 | 147
CAB_L1: ISC_116 | R2 | DB9M | 2 ; Analog Out 4-7 | D1002559 Whitening (spare chain for air to vac leapfrog) To 32 CH AA Anti Aliasing (ASC_ADC3) | C1 | DB9F | 33 ; PORT 2 | DB9 | 147
CAB_L1: ISC_117 | R4 | DB9M | 15 ; Monitor | D0901781 Common Mode Servo To 32 CH AA Anti Aliasing (LSC_ADC0) | C1 | DB9F | 9 ; PORT 6 | DB9 | 144
CAB_L1: ISC_118 | R4 | DB9M | 37 ; DC Output Head 1 | D1101906 WFS RFPD Interface To 32 CH AA (ASC_ADC5), in-air WFS | C1 | DB9F | 30 ; PORT 1 | DB9 | 144
CAB_L1: ISC_119 | R4 | DB9M | 37 ; DC Output Head 2 | D1101906 WFS RFPD Interface To 32 CH AA (ASC_ADC5), in-air WFS | C1 | DB9F | 30 ; PORT 2 | DB9 | 144
CAB_L1: ISC_120 | R4 | DB9M | 38 ; Analog Outputs to AA | D1102079 LSC RFPD INTERFACE To 32 CH AA Anti Aliasing (LSC_ADC0) | C1 | DB9F | 9 ; PORT 2 | DB9 | 144
CAB_L1: ISC_121 | R4 | DB37M | 15 ; Controls 1 | D0901781 Common Mode Servo To D1002961 Beckhoff EtherCAT 1 (CM Servo, VCO, Delay Line) ; PORT 8 | C2 | DB37F | 19 ; PORT 8 | DB37 | 142
CAB_L1: ISC_122 | R4 | DB37M | 15 ; Controls 2 | D0901781 Common Mode Servo To D1002961 Beckhoff EtherCAT 1 (CM Servo, VCO, Delay Line) ; PORT 9 | C2 | DB37F | 19 ; PORT 9 | DB37 | 142
CAB_L1: ISC_123 | R3 | DB37M | 10; Board 1, From Binary Output Module | D1002559 ISC Whitening (LSC ASAIR A 45MHz, LSC ASAIRB 18MHz, LSC ASAIR B 90MHz)To D1100251 384 Channel Binary Output (BO4) Whitening ; CHASSIS 2-1 | C2 | DB37M | 26 ; CHASSIS 2-1 | DB37 | 126
CAB_L1: ISC_124 | R3 | DB37M | 10; Board 2, From Binary Output Module | D1002559 ISC Whitening (LSC ASAIR A 45MHz, LSC ASAIRB 18MHz, LSC ASAIR B 90MHz) To D1100251 384 Channel Binary Output (BO4) Whitening ; CHASSIS 2-2 | C2 | DB37M | 26 ; CHASSIS 2-2 | DB37 | 126
CAB_L1: ISC_125 | R4 | DB9M | 23 ; PD Out (Ch 1-4) | D1002818 SUS Sat Amp (Ham 1 REFL Tip/Tilt 1) To 32 CH AA Anti Aliasing (ASC_ADC7) | C1 | DB9F | 27 ; PORT 4 | DB9 | 144
CAB_L1: ISC_126 | R4 | DB9M | 23 ; PD Out (Ch 5-8) | D1002818 SUS Sat Amp (Ham 1 REFL Tip/Tilt 2) To 32 CH AA Anti Aliasing (ASC_ADC7) | C1 | DB9F | 27 ; PORT 5 | DB9 | 144
CAB_L1: ISC_127 | R5 | DB9M | 28 ; PD Out, Channels 1-4 | D1002818 ISC 8 Channel Sat Amp (HAM6 AS Tip/Tilt1) To 32 CH AA Anti Aliasing (ASC_ADC7) | C1 | DB9F | 27 ; PORT 1 | DB9 | 127
CAB_L1: ISC_128 | R5 | DB9M | 28 ; PD Out, Channels 5-8 | D1002818 ISC 8 Channel Sat Amp (HAM6 AS Tip/Tilt2) To 32 CH AA Anti Aliasing (ASC_ADC7) | C1 | DB9F | 27 ; PORT 2 | DB9 | 127
CAB_L1: ISC_129 | R5 | DB9M | 26 ; PD Out, Channels 1-4 | D1002818 ISC 8 Channel Sat Amp (HAM6 AS Tip/Tilt3) To 32 CH AA Anti Aliasing (ASC_ADC7) | C1 | DB9F | 27 ; PORT 3 | DB9 | 127
CAB_L1: ISC_130 | R5 | DB9M | 30 ; DC Outputs Head 1 | D1101906 WFS RFPD Interface To 32 CH AA Anti Aliasing (ASC_ADC5), in-air WFS | C1 | DB9F | 30 ; PORT 3 | DB9 | 127
CAB_L1: ISC_131 | R5 | DB9M | 30 ; DC Outputs Head 2 | D1101906 WFS RFPD Interface To 32 CH AA Anti Aliasing (ASC_ADC5), in-air WFS | C1 | DB9F | 30 ; PORT 4 | DB9 | 127
CAB_L1: ISC_132 | R3 | DB25M | 37; Controls | D1000124 9.099/8.684 Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 2-8 | C3 | DB25F | 16 ; PORT 8 | DB25 | 128
CAB_L1: ISC_133 | R3 | DB25M | 35; Controls | D1000124 36 Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 2-10 | C3 | DB25F | 16 ; PORT 10 | DB25 | 128
CAB_L1: ISC_134 | R3 | DB25M | 33; Controls | D1000124 45 Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 2-9 | C3 | DB25F | 16 ; PORT 9 | DB25 | 128
CAB_L1: ISC_135 | C3 | DB25M | 30 ; Controls | D1000124 21.5Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 1-10 | C3 | DB25F | 18 ; PORT 10 | DB25 | 10
CAB_L1: ISC_136 | C3 | DB25M | 27 ; Controls | D1000124 35.5Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 1-11 | C3 | DB25F | 18 ; PORT 11 | DB25 | 10
CAB_L1: ISC_137 | C3 | DB25M | 23 ; Controls | D1000124 80Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 1-12 | C3 | DB25F | 18 ; PORT 12 | DB25 | 10
CAB_L1: ISC_138 | C3 | DB25M | 21 ; Controls | D1000124 40Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 2-2 | C3 | DB25F | 16 ; PORT 2 | DB25 | 10
CAB_L1: ISC_139 | C3 | DB25M | 19 ; Controls | D1000124 10Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 2-4 | C3 | DB25F | 16 ; PORT 4 | DB25 | 10
CAB_L1: ISC_140 | R5 | DB9F | 34 ; PORT 1A | D1100696 ASC Demod Concentrator 5 To D0902796 WFS I&Q Demodulator (Spare Chain for air to vac leapfrog) | R3 | DB9M | 21 ; Ch 1&2 | DB9 | 14
CAB_L1: ISC_141 | R5 | DB9F | 34 ; PORT 2A | D1100696 ASC Demod Concentrator 5 To D0902796 WFS I&Q Demodulator (Spare Chain for air to vac leapfrog) | R3 | DB9M | 21 ; Ch 3&4 | DB9 | 14
CAB_L1: ISC_142 | R5 | DB9F | 35 ; PORT 1A | D1100696 ASC Demod Concentrator 4 To D0902796 WFS I&Q Demodulator (ASC ASAIR A 45MHz) | R3 | DB9M | 27 ; Ch 1&2 | DB9 | 14
CAB_L1: ISC_143 | R5 | DB9F | 35 ; PORT 2A | D1100696 ASC Demod Concentrator 4 To D0902796 WFS I&Q Demodulator (ASC ASAIR A 45MHz) | R3 | DB9M | 27 ; Ch 3&4 | DB9 | 14
CAB_L1: ISC_144 | R5 | DB9F | 35 ; PORT 3A | D1100696 ASC Demod Concentrator 4 To D0902796 WFS I&Q Demodulator (ASC ASAIR A 36MHz) | R3 | DB9M | 29 ; Ch 1&2 | DB9 | 14
CAB_L1: ISC_145 | R5 | DB9F | 35 ; PORT 4A | D1100696 ASC Demod Concentrator 4 To D0902796 WFS I&Q Demodulator (ASC ASAIR A 36MHz) | R3 | DB9M | 29 ; Ch 3&4 | DB9 | 14
CAB_L1: ISC_146 | R5 | DB9F | 35 ; PORT 1B | D1100696 ASC Demod Concentrator 4 To D0902796 WFS I&Q Demodulator (ASC ASAIR B 45MHz) | R3 | DB9M | 14 ; Ch 1&2 | DB9 | 14
CAB_L1: ISC_147 | R5 | DB9F | 35 ; PORT 2B | D1100696 ASC Demod Concentrator 4 To D0902796 WFS I&Q Demodulator (ASC ASAIR B 45MHz) | R3 | DB9M | 14 ; Ch 3&4 | DB9 | 14
CAB_L1: ISC_148 | R5 | DB9F | 35 ; PORT 3B | D1100696 ASC Demod Concentrator 4 To D0902796 WFS I&Q Demodulator (ASC ASAIR B 36MHz) | R3 | DB9M | 16 ; Ch 1&2 | DB9 | 14
CAB_L1: ISC_149 | R5 | DB9F | 35 ; PORT 4B | D1100696 ASC Demod Concentrator 4 To D0902796 WFS I&Q Demodulator (ASC ASAIR B 36MHz) | R3 | DB9M | 16 ; Ch 3&4 | DB9 | 14
CAB_L1: ISC_150 | R5 | DB9F | 36 ; Demodulator 3 | D1100691 LSC Demod Concentrator 4 To D0902796 WFS I&Q Demodulator (LSC ASAIR A 45MHz, LSC ASAIRB 18MHz, LSC ASAIR B 90MHz) | R3 | DB9M | 8 ; Ch 1&2 | DB9 | 14
CAB_L1: ISC_151 | R5 | DB9F | 36 ; Demodulator 4 | D1100691 LSC Demod Concentrator 4 To D0902796 WFS I&Q Demodulator (LSC ASAIR A 45MHz, LSC ASAIRB 18MHz, LSC ASAIR B 90MHz) | R3 | DB9M | 8 ; Ch 3&4 | DB9 | 14
CAB_L1: ISC_152 | C4 | DB25M | 9 ; Controls | D1000124 71Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 1-9 | C3 | DB25F | 18 ; PORT 9 | DB25 | 12
CAB_L1: ISC_153 | C4 | DB25M | 12 ; Controls | D1000124 24.078/22.993 Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 1-8 | C3 | DB25F | 18 ; PORT 8 | DB25 | 12
CAB_L1: ISC_154 | C4 | DB25M | 26 ; Controls | D1000124 9.099/8.684Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 1-1 | C3 | DB25F | 18 ; PORT 1 | DB25 | 12
CAB_L1: ISC_155 | C4 | DB25M | 22 ; Controls | D1000124 18Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 1-2 | C3 | DB25F | 18 ; PORT 2 | DB25 | 12
CAB_L1: ISC_156 | C4 | DB25M | 21 ; Controls | D1000124 27Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 1-3 | C3 | DB25F | 18 ; PORT 3 | DB25 | 12
CAB_L1: ISC_157 | C4 | DB25M | 20 ; Controls | D1000124 36Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 1-4 | C3 | DB25F | 18 ; PORT 4 | DB25 | 12
CAB_L1: ISC_158 | C4 | DB25M | 19 ; Controls | D1000124 45Mhz RF Distribution Amp To D1100262 RF Amp Concentrator 1-5 | C3 | DB25F | 18 ; PORT 5 | DB25 | 12
CAB_L1: ISC_159 | R4 | DB9M | 26 ; Analog Out 0-3 | D1002559 Whitening (Ham 3; ISC-ASC_POP) To 32 CH AA (ASC_ADC6) | C1 | DB9F | 28 ; PORT 1 | DB9 | 144
CAB_L1: ISC_160 | R4 | DB9M | 26 ; Analog Out 4-7 | D1002559 Whitening (Ham 3; ISC-ASC_POP) To 32 CH AA (ASC_ADC6) | C1 | DB9F | 28 ; PORT 2 | DB9 | 144
CAB_L1: ISC_161 | R5 | DB9M | 22 ; Analog Out 0-3 | D1002559 Whitening/VGA (ASC OMCR A&B) To 32 CH AA (ASC_ADC6) | C1 | DB9F | 28 ; PORT 6 | DB9 | 127
CAB_L1: ISC_162 | R5 | DB9M | 22 ; Analog Out 4-7 | D1002559 Whitening/VGA (ASC OMCR A&B) To 32 CH AA (ASC_ADC6) | C1 | DB9F | 28 ; PORT 7 | DB9 | 127
CAB_L1: ISC_163 | R5 | DB9M | 18 ; Analog Out 0-3 | D1002559 Whitening/VGA (ASC AS C) To 32 CH AA (ASC_ADC6) | C1 | DB9F | 28 ; PORT 3 | DB9 | 127
CAB_L1: ISC_164 | R3 | DB9M | 23 ; Analog Out 0-3 | D1002559 Whitening (Spare Chain for air to vac leapfrog) To 32 CH AA (ASC_ADC3) | C1 | DB9F | 33 ; PORT 3 | DB9 | 124
CAB_L1: ISC_165 | R3 | DB9M | 23 ; Analog Out 4-7 | D1002559 Whitening (Spare Chain for air to vac leapfrog) To 32 CH AA (ASC_ADC3) | C1 | DB9F | 33 ; PORT 4 | DB9 | 124
CAB_L1: ISC_166 | R3 | DB9M | 25 ; Analog Out 0-3 | D1002559 Whitening (ASC ASAIR A 45MHz) To 32 CH AA (ASC_ADC4) | C1 | DB9F | 31 ; PORT 1 | DB9 | 124
CAB_L1: ISC_167 | R3 | DB9M | 25 ; Analog Out 4-7 | D1002559 Whitening (ASC ASAIR A 45MHz) To 32 CH AA (ASC_ADC4) | C1 | DB9F | 31 ; PORT 2 | DB9 | 124
CAB_L1: ISC_168 | R3 | DB9M | 31 ; Analog Out 0-3 | D1002559 Whitening (ASC ASAIR A 36MHz) To 32 CH AA (ASC_ADC4) | C1 | DB9F | 31 ; PORT 3 | DB9 | 124
CAB_L1: ISC_169 | R3 | DB9M | 31 ; Analog Out 4-7 | D1002559 Whitening (ASC ASAIR A 36MHz) To 32 CH AA (ASC_ADC4) | C1 | DB9F | 31 ; PORT 4 | DB9 | 124
CAB_L1: ISC_170 | R3 | DB9M | 12 ; Analog Out 0-3 | D1002559 Whitening (ASC ASAIR B 45MHz) To 32 CH AA (ASC_ADC4) | C1 | DB9F | 31 ; PORT 5 | DB9 | 124
CAB_L1: ISC_171 | R3 | DB9M | 12 ; Analog Out 4-7 | D1002559 Whitening (ASC ASAIR B 45MHz) To 32 CH AA (ASC_ADC4) | C1 | DB9F | 31 ; PORT 6 | DB9 | 124
CAB_L1: ISC_172 | R3 | DB9M | 18 ; Analog Out 0-3 | D1002559 Whitening (ASC ASAIR B 36MHz) To 32 CH AA (ASC_ADC4) | C1 | DB9F | 31 ; PORT 7 | DB9 | 124
CAB_L1: ISC_173 | R3 | DB9M | 18 ; Analog Out 4-7 | D1002559 Whitening (ASC ASAIR B 36MHz) To 32 CH AA (ASC_ADC4) | C1 | DB9F | 31 ; PORT 8 | DB9 | 124
CAB_L1: ISC_174 | R3 | DB9M | 10 ; Analog Out 0-3 | D1002559 Whitening (LSC ASAIR A 45MHz, LSC ASAIRB 19MHz, LSC ASAIR B 90MHz) To 32 CH AA Anti Aliasing (LSC_ADC1) | C1 | DB9F | 8 ; PORT 3 | DB9 | 124
CAB_L1: ISC_175 | R3 | DB9M | 10 ; Analog Out 4-7 | D1002559 Whitening (LSC ASAIR A 45MHz, LSC ASAIRB 19MHz, LSC ASAIR B 90MHz) To 32 CH AA Anti Aliasing (LSC_ADC1) | C1 | DB9F | 8 ; PORT 4 | DB9 | 124
CAB_L1: ISC_176 | C4 | DB25M | 18 ; Controls | D1000124 90MHz RF Distribution Amp To D1100262 RF Amp Concentrator 1-6 | C3 | DB25F | 18 ; PORT 6 | DB25 | 12
CAB_L1: ISC_177 | C4 | DB25M | 17 ; Controls | D1000124 135 Mhz RF Distribution Amp To RF Amp Concentrator 1-7 | C3 | DB25F | 18 ; PORT 7 | DB25 | 12
CAB_L1: ISC_178 | IOT2L | DB25M | Controller 3; PORT 1 (Controls) | D1100323 Picomotor Interface (#3) (Ham1 & HAM3) To D1100680 Beckhoff EtherCAT 2 (Picomotor, Serial Ports, Modbus) | C2 | DB25F | 15 ; PORT 1 (Readback) | DB25 | 142
CAB_L1: ISC_179 | IOT2L | DB25F | Controller 3; PORT 2 (Readback) | D1100323 Picomotor Interface (#3) (Ham1 & HAM3) To D1100680 Beckhoff EtherCAT 2 (Picomotor, Serial Ports, Modbus) | C2 | DB25M | 15 ; PORT 1 (Control) | DB25 | 142
CAB_L1: ISC_180 | IOT2L | DB25M | Controller 4; PORT 1 (Controls) | D1100323 Picomotor Controler (#4) (ISCT1 & IOT2L) To D1100680 Beckhoff EtherCAT 2 (Picomotor, Serial Ports, Modbus) | C2 | DB25F | 15 ; PORT 4 (Readback) | DB25 | 142
CAB_L1: ISC_181 | IOT2L | DB25F | Controller 4; PORT 2 (Readback) | D1100323 Picomotor Controler (#4) (ISCT1 & IOT2L) To D1100680 Beckhoff EtherCAT 2 (Picomotor, Serial Ports, Modbus) | C2 | DB25M | 15 ; PORT 4 (Control) | DB25 | 142
CAB_L1: ISC_182 | ISCT6 | DB25M | Controller 7; PORT 1 (Controls) | D1100323 Picomotor Controler (#7) (HAM6 & ISCT6) To D1100680 Beckhoff EtherCAT 2 (Picomotor, Serial Ports, Modbus) | C2 | DB25F | 15 ; PORT 3 (Readback) | DB25 | 129
CAB_L1: ISC_183 | ISCT6 | DB25F | Controller 7; PORT 2 (Readback) | D1100323 Picomotor Controler (#7) (HAM6 & ISCT6) To D1100680 Beckhoff EtherCAT 2 (Picomotor, Serial Ports, Modbus) | C2 | DB25M | 15 ; PORT 3 (Control) | DB25 | 129
CAB_L1: ISC_184 | C1 | DB9F | 30 ; PORT 7 | D0902783 ASC 32 Ch AA (ASC_ADC5-7) Anti Alias To D1100687 4 CH Coil Driver (Tip/Tilt REFL) | C1 | DB9M | 25 ; Monitors | DB9 | 6
CAB_L1: ISC_185 | C1 | DB9F | 30 ; PORT 8 | D0902783 ASC 32 Ch AA (ASC_ADC5-8) Anti Alias To D1100687 4 CH Coil Driver (Tip/Tilt REFL) | C1 | DB9M | 24 ; Monitors | DB9 | 6
CAB_L1: ISC_186 | C1 | DB9F | 27 ; PORT 6 | D0902783 ASC 32 Ch AA (ASC_ADC7-6) Anti Alias To D1100687 4 CH Coil Driver (Tip/Tilt REFL) | C1 | DB9M | 22 ; Monitors | DB9 | 6
CAB_L1: ISC_187 | C1 | DB9F | 27 ; PORT 7 | D0902783 ASC 32 Ch AA (ASC_ADC7-7) Anti Alias To D1100687 4 CH Coil Driver (Tip/Tilt REFL) | C1 | DB9M | 21 ; Monitors | DB9 | 6
CAB_L1: ISC_188 | C1 | DB9F | 27 ; PORT 8 | D0902783 ASC 32 Ch AA (ASC_ADC7-8) Anti Alias To D1100687 4 CH Coil Driver (Tip/Tilt REFL) | C1 | DB9M | 19 ; Monitors | DB9 | 6
CAB_L1: ISC_189 | C1 | DB9F | 18 ; Ch 1-4 | D070081 ASC 16 Ch AA (ASC_DAC0-1) Anti Image To D1100687 4 CH Coil Driver (Tip/Tilt OMC) ; Ch 1-4 | C1 | DB9M | 22 ; Coil Inputs | DB9 | 6
CAB_L1: ISC_190 | C1 | DB9F | 18 ; Ch 5-8 | D070081 ASC 16 Ch AA (ASC_DAC0-2) Anti Image To D1100687 4 CH Coil Driver (Tip/Tilt OMC) ; Ch 5-8 | C1 | DB9M | 21 ; Coil Inputs | DB9 | 6
CAB_L1: ISC_191 | C1 | DB9F | 18 ; Ch 9-13 | D070081 ASC 16 Ch AA (ASC_DAC0-3) Anti Image To D1100687 4 CH Coil Driver (Tip/Tilt OMC) ; Ch 9-13 | C1 | DB9M | 19 ; Coil Inputs | DB9 | 6
CAB_L1: ISC_192 | C1 | DB9F | 16 ; Ch 1-4 | D070081 ASC 16 Ch AA (ASC_DAC1-1) Anti Image To D1100687 4 CH Coil Driver (Tip/Tilt REFL) ; Ch 1-4 | C1 | DB9M | 25 ; Coil Inputs | DB9 | 6
CAB_L1: ISC_193 | C1 | DB9F | 16 ; Ch 5-8 | D070081 ASC 16 Ch AA (ASC_DAC1-2) Anti Image To D1100687 4 CH Coil Driver (Tip/Tilt REFL) ; Ch 5-8 | C1 | DB9M | 24 ; Coil Inputs | DB9 | 6
CAB_L1: ISC_194 | R4 | DB9F | 23 ; Coil Drive In (Ch 1-4) | D1002818 SUS Sat Amp (Ham 1 Tip/Tilt) To D1100687 4 CH Coil Driver (Tip/Tilt REFL) | C1 | DB15M | 25 ; Coil Driver Out | DB9 | 144
CAB_L1: ISC_195 | R4 | DB9F | 23 ; Coil Drive In (Ch 5-8) | D1002818 SUS Sat Amp (Ham 1 Tip/Tilt) To D1100687 4 CH Coil Driver (Tip/Tilt REFL) | C1 | DB15M | 24 ; Coil Driver Out | DB9 | 144
CAB_L1: ISC_196 | R5 | DB9F | 28 ; Coil Drive In, Ch 1-4 | D1002818 ISC 8 Channel Sat Amp (Tip/Tilt) To D1100687 4 CH Coil Driver (Tip/Tilt OMC) | C1 | DB15M | 22 ; Coil Driver Out | DB9 | 127
CAB_L1: ISC_197 | R5 | DB9F | 28 ; Coil Drive In, Ch 5-8 | D1002818 ISC 8 Channel Sat Amp (Tip/Tilt) To D1100687 4 CH Coil Driver (Tip/Tilt OMC) | C1 | DB15M | 21 ; Coil Driver Out | DB9 | 127
CAB_L1: ISC_198 | R5 | DB9F | 26 ; Coil Drive In, Ch 1-4 | D1002818 ISC 8 Channel Sat Amp (Tip/Tilt) To D1100687 4 CH Coil Driver (Tip/Tilt OMC) | C1 | DB15M | 19 ; Coil Driver Out | DB9 | 127
CAB_L1: ISC_199 | R4 | DB37M | 42 ; Controls | D1100691 LSC Demod Concentrator 2 To D1100681 Beckhoff EtherCAT 3-2 (LSC Demod, Serial VCO, Delay Line, RF Amps) | C2 | DB37F | 11 ; PORT 2 | DB37 | 142
CAB_L1: ISC_200 | R4 | DB37M | 41 ; Controls | D1100691 LSC Demod Concentrator 3 To D1100681 Beckhoff EtherCAT 3-2 (LSC Demod, Serial VCO, Delay Line, RF Amps) | C2 | DB37F | 11 ; PORT 3 | DB37 | 142
CAB_L1: ISC_201 | R4 | DB37M | 40; PORT CTRL A | D1100696 ASC Demod Concentrator 2-A To D1101266 Beckhoff EtherCAT 4-2 (ASC Demod) | C2 | DB37F | 6 ; PORT 2 | DB37 | 142
CAB_L1: ISC_202 | R4 | DB37M | 40; PORT CTRL B | D1100696 ASC Demod Concentrator 2-B To D1101266 Beckhoff EtherCAT 4-3 (ASC Demod) | C2 | DB37F | 6 ; PORT 3 | DB37 | 142
CAB_L1: ISC_203 | R5 | DB37M | 36; PORT CTRL | D1100691 LSC Demod Concentrator 4 To D1100681 Beckhoff EtherCAT 3-4 (LSC Demod, Serial VCO, Delay Line, RF Amps) | C2 | DB37F | 11 ; PORT 4 | DB37 | 129
CAB_L1: ISC_204 | R5 | DB37M | 35; PORT CTRL A | D1100696 ASC Demod Concentrator 4-A To D1101266 Beckhoff EtherCAT 4-6 (ASC Demod) | C2 | DB37F | 6 ; PORT 6 | DB37 | 129
CAB_L1: ISC_205 | R5 | DB37M | 35; PORT CTRL B | D1100696 ASC Demod Concentrator 4-B To D1101266 Beckhoff EtherCAT 4-7 (ASC Demod) | C2 | DB37F | 6 ; PORT 7 | DB37 | 129
CAB_L1: ISC_206 | R1 | DB25F | 21 ; Controls 2 | D0900128 24.078MHz Dual Delay Line To D1002961 Beckhoff EtherCAT 1-4 (CM Servo, VCO, Delay Line) | C2 | DB25M | 19 ; PORT 4 | DB25 | 147
CAB_L1: ISC_207 | R5 | DB37M | 34; PORT CTRL A | D1100696 ASC Demod Concentrator 5-A To D1101266 Beckhoff EtherCAT 4-7 (ASC Demod) | C2 | DB37F | 6 ; PORT 8 | DB37 | 129
CAB_L1: ISC_208 | C3 | DB25M | 22 ; Controls | D1002182 40MHz Output, Frequency Divider (divide by 2) to D1100262 RF Amp Concentrator 2-1 | C3 | DB25F | 16 ; PORT 1 | DB25 | 6
CAB_L1: ISC_209 | C3 | DB25M | 20 ; Controls | D1100974 10MHz Output, Frequency Divider (divide by 8) to D1100262 RF Amp Concentrator 2-3 | C3 | DB25F | 16 ; PORT 3 | DB25 | 6
CAB_L1: ISC_210 | R5 | DB37M | 34; PORT CTRL B | D1100696 ASC Demod Concentrator 5-B To D1101266 Beckhoff EtherCAT 4-9 (ASC Demod) | C2 | DB37F | 6 ; PORT 9 | DB37 | 129
CAB_L1: ISC_211 | R1 | DB9M | 14 ; Analog Output to AA | D1102079 LSC RF PD INTERFACE To 32 CH AA Anti Aliasing (LSC_ADC0_8); THIS IS IN USE!! | C1 | DB9F | 6 ; In 1-4 | DB9 | 149
CAB_L1: ISC_212 | IOT2L | DB9M | IMC_PDH FLANGE | IOT2L IMC_PDH Flange To IMC_PDH | IOT2L | DB9F | IMC_PDH | DB9 | 10
CAB_L1: ISC_213 | IOT2L | DB15M | IMC_WFS_A FLANGE | IOT2L IMC_WFS_A Flange To IOT2L IMC_WFS_A | IOT2L | DB15F | IMC_WFS_A | DB15 | 10
CAB_L1: ISC_214 | IOT2L | DB15M | IMC_WFS_A FLANGE | IOT2L IMC_WFS_B Flange To IOT2L IMC_WFS_B | IOT2L | DB15F | IMC_WFS_A | DB15 | 10
CAB_L1: ISC_215 | ISCT1 | DB9M | LSC_POPAIR_A FLANGE | ISCT1 LSC_POPAIR_A FLANGE To LSC_POPAIR_A | ISCT1 | DB9F | LSC_POPAIR_A | DB9 | 14
CAB_L1: ISC_216 | ISCT1 | DB9M | LSC_REFLAIR_A FLANGE | ISCT1 LSC_REFLAIR_A FLANGE To LSC_REFLAIR_A | ISCT1 | DB9F | LSC_REFLAIR_A | DB9 | 14
CAB_L1: ISC_217 | HAM1 | DB25F | LSC_POP FLANGE D5-1C2 IN VACCUMN | HAM1 LSC_POP FLANGE To LSC_POP IN VACCUMN | HAM1 | DB25M | LSC_POP | DB9 | 0
CAB_L1: ISC_218 | HAM1 | DB25F | LSC_REFL FLANGE D5-1C1 IN VACCUMN | HAM1 LSC_REFL FLANGE To LSC_REFL IN VACCUMN | HAM1 | DB25M | LSC_REFL | DB9 | 0
CAB_L1: ISC_219 | ISCT1 | DB9F | LSC_REFLAIR_A FLANGE | ISCT1 LSC_REFLAIR_A FLANGE To D1102079 LSC RF PD INTERFACE | R4 | DB9M | 38 ; RF1 | DB9 | 40
CAB_L1: ISC_220 | ISCT1 | DB9F | LSC_POPAIR_A FLANGE | ISCT1 LSC_POPAIR_A FLANGE To D1102079 LSC RF PD INTERFACE | R4 | DB9M | 38 ; RF2 | DB9 | 40
CAB_L1: ISC_221 | HAM1 | DB25F | LSC_POP FLANGE D5-1C2 | HAM1 LSC_POP FLANGE To D1102079 LSC RF PD INTERFACE | R4 | DB9M | 38 ; RF3 | DB9 | 38
CAB_L1: ISC_222 | HAM1 | DB25F | LSC_REFL FLANGE D5-1C1 | HAM1 LSC_REFL FLANGE To D1102079 LSC RF PD INTERFACE | R4 | DB9M | 38 ; RF4 | DB9 | 38
CAB_L1: ISC_223 | HAM1 | DB25F | ASC_REFL_A FLANGE D6-1C1 | HAM1 ASC_REFL_A FLANGE FLANGE To D1101906 WFS Interface | R4 | DB15M | 37 ; WFS Head 1 | DB15 | 38
CAB_L1: ISC_224 | HAM1 | DB25F | ASC_REFL_B FLANGE D6-1C2 | HAM1 ASC_REFL_B FLANGE FLANGE To D1101906 WFS Interface | R4 | DB15M | 37 ; WFS Head 2 | DB15 | 38
CAB_L1: ISC_225 | HAM1 | DB25F | ASC_REFL_A FLANGE D6-1C1 IN VACCUMN | HAM1 ASC_REFL_A FLANGE To ASC_REFL_A FLANGE IN VACCUMN | HAM1 | DB25M | ASC_REFL_A | DB25 | 0
CAB_L1: ISC_226 | HAM1 | DB25F | ASC_REFL_B FLANGE D6-1C2 IN VACCUMN | HAM1 ASC_REFL_B FLANGE To ASC_REFL_B FLANGE IN VACCUMN | HAM1 | DB25M | ASC_REFL_B | DB25 | 0
CAB_L1: ISC_227 | HAM1 | DB25F | PICOMOTORS D4-1C1 | HAM1 PICOMOTOR FLANGE To D1100323 Picomotor Interface #3 (Ham 1/Ham3) | IOT2L | DB25M | Pcont #3; Channels 1-4 | DB25 | 42
CAB_L1: ISC_228 | HAM1 | DB25F | ISC-REFL TIP/TILT1 D5-3C1 | HAM1 ISC-REFL TIP/TILT1 To D1002818 WFS SUS Sat Amp (Ham 1 Tilt/Tilt) | R4 | DB25M | 23 ; Ch 1-4 | DB25 | 38
CAB_L1: ISC_229 | HAM1 | DB25F | ISC-REFL TIP/TILT1 D5-3C2 | HAM1 ISC-REFL TIP/TILT2 To D1002818 WFS SUS Sat Amp (Ham 1 Tilt/Tilt) | R4 | DB25M | 23 ; Ch 5-8 | DB25 | 38
CAB_L1: ISC_230 | HAM3 | DB25F | PICOMOTORS D3-3C1 | HAM3 PICOMOTORS To D1100323 Picomotor Interface #3 (Ham 1/Ham3) | IOT2L | DB25M | Pcont #3; Channels 5-8 | DB25 | 120
CAB_L1: ISC_231 | HAM3 | DB25F | ISC-QUAD DIODE ASC_POP D3-3C2 | HAM3 ISC-QUAD DIODE ASC_POP To D1002481 Dual QPD Transimpedance Amp (Ham 3) | R4 | DB25M | 25; PD Input | DB25 | 120
CAB_L1: ISC_232 | HAM6 | DB25F | ASC_OMCR_A & B FLANGE D6-F4 | HAM6 ASC_OMCR_A & B To D1002481 Dual QPD Amp (ASC OMCR A&B) | R5 | DB25M | 24 ; PD Input | DB25 | 25
CAB_L1: ISC_233 | HAM6 | DB25F | ASC_ASC_C FLANGE D6-F5 | HAM6 ASC_ASC_C To D1002481 Dual QPD Amp (ASC AS C) | R5 | DB25M | 20 ; PD Input | DB25 | 25
CAB_L1: ISC_234 | HAM6 | DB25F | PICOMOTORS AC_C_QPD FLANGE D6-F7 | HAM6 PICOMOTORS AC_C_QPD FLANGE To D1100323 Picomotor Controler (#7) | ISCT6 | DB25M | Pcont #7; Channels 1-4 | DB25 | 25
CAB_L1: ISC_235 | HAM6 | DB25F | PICOMOTORS RF_WAVEFRT, OMC & QPD FLANGE D6-F6 | HAM6 PICOMOTORS RF_WAVEFRT, OMC & QPD To D1100323 Picomotor Controler (#7) | ISCT6 | DB25M | Pcont #7; Channels 5-8 | DB25 | 25
CAB_L1: ISC_236 | HAM6 | DB25F | STEERING INTO OMC TIP TILT 1 FLANGE D6-F10 | HAM6 STEERING INTO OMC & QPD TIP TILT 1 To D1002818 ISC 8 Channel Sat Amp (Tip/Tilt) | R5 | DB25M | 28 ; CH 1-4 | DB25 | 25
CAB_L1: ISC_237 | HAM6 | DB25F | STEERING INTO OMC TIP TILT 2 FLANGE D6-F11 | HAM6 STEERING INTO OMC & QPD TIP TILT 2 To D1002818 ISC 8 Channel Sat Amp (Tip/Tilt) | R5 | DB25M | 28 ; CH 5-8 | DB25 | 25
CAB_L1: ISC_238 | HAM6 | DB25F | STEERING INTO OMC TIP TILT 3 FLANGE D6-F12 | HAM6 STEERING INTO OMC & QPD TIP TILT 3 To D1002818 ISC 8 Channel Sat Amp (Tip/Tilt) | R5 | DB25M | 26 ; CH 1-4 | DB25 | 25
CAB_L1: ISC_239 | ISCT6 | DB15F | ASC ASAIR_A FLANGE | ISCT6 ASC ASAIR_A FLANGE To D1101906 WFS RFPD Interface | R5 | DB15M | 30 ;To WFS Head 1 | DB15 | 25
CAB_L1: ISC_240 | ISCT6 | DB15F | ASC ASAIR_B FLANGE | ISCT6 ASC ASAIR_B FLANGE To D1101906 WFS RFPD Interface | R5 | DB15M | 30 ;To WFS Head 2 | DB15 | 25
CAB_L1: ISC_241 | ISCT6 | DB9F | LSC ASAIR_A FLANGE | ISCT6 LSC ASAIR_A FLANGE To D1102079 LSC RFPD INTERFACE | R5 | DB9M | 32 ; To LSC Head 1 | DB9 | 25
CAB_L1: ISC_242 | R5 | DB9M | 15; PD DC 1-4 IN | D1201349 EtherCAT Concentrator 4 (Photodode 1-4 IN/OUT) To 32 CH AA Anti Aliasing (LSC_ADC0) | C1 | DB9F | 9 ; PORT 3 | DB9 | 127
CAB_L1: IO_243 | HAM2 | DB25F | PICOMOTORS FLANGE D4-3C2 | HAM2 PICOMOTORS FLANGE To D1100323 Picomotor Cltr (#5) | IOT2L | DB25M | Pcont #5; channels 1-4 | DB25 | 55
CAB_L1: ISC_244 | HAM2 | DB25F | SM2 TRANS QPD FLANGE D6-F10 | HAM3 SM2 TRANS FLANGE To D1002481 Dual QPD Amp | R4 | DB25M | 31 ; PD Input | DB25 | 55
CAB_L1: IO_245 | HAM3 | DB25F | MC2 TRANS QPD FLANGE D1-3C2 | HAM3 MC2 TRANS FLANGE To D1002481 Dual QPD Amp | R4 | DB25M | 28 ; PD Input | DB25 | 135
CAB_L1: IO_246 | SPARE | DB25F | was a duplicate of 230, no longer needed | was a duplicate of 230, no longer needed | SPARE | DB25M | SPARE | DB25 | 135
CAB_L1: IO_247 | R4 | DB9M | 32 ; Analog Out 0-3 | D1002559 Whitening (ISC L1-R1) To 32 CH AA (ASC_ADC1) | C1 | DB9F | 36 (ASC_ADC1) ; PORT 1 | DB9 | 144
CAB_L1: IO_248 | R1 | DB9M | 31 DSUB1 | ASC DAC1 channels 13-16 to the right side of DSUB breakout patchpanel in the ISC-R1 rack. | C1 | DB9F | SPARE | DB9 | 144
CAB_L1: IO_249 | R4 | DB9M | 29 ; Analog Out 0-3 | D1002559 Whitening (ISC L1-R4) To 32 CH AA (ASC_ADC1) ; Currently utilized for MC2 | C1 | DB9F | 36 (ASC_ADC1) ; PORT 2 | DB9 | 144
CAB_L1: IO_250 | R1 | DB9M | 31 DSUB1 | used in R1 with DB9 breakout in U 31 ;ASC_ADC0-7 | C1 | DB9F | ASC_ADC0-7 | DB9 | 144
CAB_L1: IO_251 | R1 | DB9M | 3 ; Differential Analog Inputs | D1100482 Dif-to-SE To 16 CH AI (C1-16-3) | C1 | DB9F | 16 ; PORT 3 | DB9 | 149
CAB_L1: IO_252 | R4 | DB37M | 32 ; Board 1, From Binary Output Module | D1002559 Whitening (IM4 & ISS QPD) To D1100251 384 Channel Binary Out (BO4) ; CHASSIS 5-1 | C2 | DB37M | 26 ; CHASSIS 5-1 | DB37 | 142
CAB_L1: IO_253 | R4 | DB37M | 32 ; Board 2, From Binary Output Module | D1002559 Whitening (IM4 & ISS QPD) To D1100251 384 Channel Binary Out (BO4) ; CHASSIS 5-2 | C2 | DB37M | 26 ; CHASSIS 5-2 | DB37 | 142
CAB_L1: IO_254 | R4 | DB37M | 29 ; Board 1, From Binary Output Module | D1002559 Whitening (MC2) To D1100251 384 Channel Binary Out (BO4) ; CHASSIS 6-1 | C2 | DB37M | 26 ; CHASSIS 6-1 | DB37 | 142
CAB_L1: IO_255 | R4 | DB37M | 29 ; Board 2, From Binary Output Module | D1002559 Whitening (MC2) To D1100251 384 Channel Binary Out (BO4) ; CHASSIS 6-2 | C2 | DB37M | 26 ; CHASSIS 6-2 | DB37 | 142
CAB_L1: ISC_256 | ISCT1 | DB15F | ASC REFLAIR_A FLANGE | ISCT1 ASC REFLAIR_A FLANGE To D1101906 WFS Interface | R4 | DB15M | 37 ; To WFS Head 1 | DB15 | 40
CAB_L1: ISC_257 | ISCT1 | DB15F | ASC REFLAIR_B FLANGE | ISCT1 ASC REFLAIR_B FLANGE To D1101906 WFS Interface | R4 | DB15M | 37 ; To WFS Head 2 | DB15 | 40
CAB_L1: ISC_258 | ISCT1 | DB9M | GENERIC INTERFACE FLANGE | D1002932 Generic Interface To D1002932 Generic Interface Flange | ISCT1 | DB9F | GENERIC INTERFACE | DB9 | 15
CAB_L1: ISC_259 | R4 | DB9M | 20; PD DC 1-4 IN | D1201345 EtherCAT Concentrator 3 (Photodode 1-4 IN/OUT) To 32 CH AA Anti Aliasing (LSC_ADC_1) | C1 | DB9F | 9 ; PORT 1 | DB9 | 147
CAB_L1: IO_260 | ISCT6 | DB9M | GENERIC INTERFACE FLANGE | D1002932 Generic Interface To D1002932 Generic Interface Flange | ISCT6 | DB9F | GENERIC INTERFACE | DB9 | 15
CAB_L1: ISC_261 | R4 | DB37M | This cable was a duplicate of cable 178 | This cable was a duplicate of cable 178 | C2 | DB37F | SPARE | DB37 | 142
CAB_L1: ISC_262 | ISCT6 | DB15F | ASC REFLAIR_A FLANGE | ASC ASAIR_A To ASC ASAIR_A FLANGE | ISCT6 | DB15M | ASC ASAIR_A | DB15 | 15
CAB_L1: ISC_263 | ISCT6 | DB15F | ASC REFLAIR_B FLANGE | ASC ASAIR_B To ASC ASAIR_B FLANGE | ISCT6 | DB15M | ASC ASAIR_B | DB15 | 15
CAB_L1: ISC_264 | ISCT6 | DB9F | LSC ASAIR_A FLANGE | ISCT6 LSC ASAIR_A To LSC ASAIR_A FLANGE | ISCT6 | DB9M | LSC ASAIR_A | DB9 | 15
CAB_L1: ISC_265 | HAM6 | DB25F | ASC_AS_A FLANGE D5-3C1 | HAM6 ASC_AS_A FLANGE FLANGE To D1101906 WFS Interface | R5 | DB15M | 30 : To WFS Head 1 | DB15 | 25
CAB_L1: ISC_266 | HAM6 | DB25F | ASC_AS_B FLANGE D5-3C2 | HAM6 ASC_AS_B FLANGE FLANGE To D1101906 WFS Interface | R5 | DB15M | 30 : To WFS Head 2 | DB15 | 25
CAB_L1: IO_267 | PSL/IO TABLE | DB9F | Generic Interface FLANGE | PSL/IO TABLE D1002932 Generic Interface To PSL/IOT2L D1002932 Generic Interface FLANGE | PSL/IO TABLE | DB9M | Generic Interface | DB9 | 15
CAB_L1: IO_268 | PSL/IO TABLE | DB9M | Generic Interface FLANGE | PSL/IO TABLE D1002932 Generic Interface FLANGE To 32 CH AA Anti Aliasing (ASC_ADC_1_3) | C1 | DB9F | 36 (ASC_ADC1) ; PORT 3 | DB9 | 149
CAB_L1: IO_269 | IOT2L | DB9F | Generic Interface FLANGE | IOT2L TABLE D1002932 Generic Interface To IOT2L TABLE D1002932 Generic Interface FLANGE | IOT2L | DB9M | Generic Interface | DB9 | 15
CAB_L1: IO_270 | IOT2L | DB9F | Generic Interface FLANGE | IOT2L TABLE D1002932 Generic Interface FLANGE To 32 CH AA Anti Aliasing (ASC_ADC1) | C1 | DB9M | 36 (ASC_ADC1) ; PORT 4 | DB9 | 137
CAB_L1: IO_271 | IOT2R TABLE | DB9F | Generic Interface FLANGE | IOT2R TABLE D1002932 Generic Interface To IOT2R TABLE D1002932 Generic Interface FLANGE | IOT2R TABLE | DB9M | Generic Interface | DB9 | 15
CAB_L1: IO_272 | IOT2R TABLE | DB9M | Generic Interface FLANGE | IOT2R TABLE D1002932 Generic Interface FLANGE To 32 CH AA Anti Aliasing (ASC_ADC1) | C1 | DB9F | 36 (ASC_ADC1) ; PORT 5 | DB9 | 140
CAB_L1: ISC_273 | ISCT1 | DB15F | ASC REFLAIR_A FLANGE | ISCT1 ASC REFLAIR_A To ISCT1 ASC REFLAIR_A FLANGE | ISCT1 | DB15M | ASC REFLAIR_A | DB15 | 15
CAB_L1: ISC_274 | ISCT1 | DB15F | ASC REFLAIR_B FLANGE | ISCT1 ASC REFLAIR_B To ISCT1 ASC REFLAIR_B FLANGE | ISCT1 | DB15M | ASC REFLAIR_B | DB15 | 15
CAB_L1: IO_275 | SPARE | DB37M | SPARE | SPARE | SPARE | DB37F | SPARE | DB37 | 142
CAB_L1: ISC_276 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 4 ; PORT 1 | 32 CH AA Anti Aliasing (LSC) To 32 ch ADC ADC_0 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 9 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_277 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 4 ; PORT 3 | 32 CH AA Anti Aliasing (LSC) To 32 ch ADC ADC_1 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 8 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_278 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 4 ; PORT 2 | 16 CH AA Anti Image (LSC) To 16 ch ADC DAC_0 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 4 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_279 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 13 ; PORT 1 | 32 CH AA Anti Aliasing (ASC) To 32 ch ADC ADC_0 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 37 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_280 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 13 ; PORT 3 | 32 CH AA Anti Aliasing (ASC) To 32 ch ADC ADC_1 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 36 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_281 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 13 ; PORT 4 | 32 CH AA Anti Aliasing (ASC) To 32 ch ADC ADC_2 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 34 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_282 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 13 ; PORT 5 | 32 CH AA Anti Aliasing (ASC) To 32 ch ADC ADC_3 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 33 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_283 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 13 ; PORT 6 | 32 CH AA Anti Aliasing (ASC) To 32 ch ADC ADC_4 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 31 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_284 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 13 ; PORT 7 | 32 CH AA Anti Aliasing (ASC) To 32 ch ADC ADC_5 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 30 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_285 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 13 ; PORT 8 | 32 CH AA Anti Aliasing (ASC) To 32 ch ADC ADC_6 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 28 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_286 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 13 ; PORT 9 | 32 CH AA Anti Aliasing (ASC) To 32 ch ADC ADC_7 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 27 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_287 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 13 ; PORT 2 | 16 CH AI Anti Image (ASC) To 16 ch DAC DAC_0 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 18 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_288 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 13 ; PORT 10 | 16 CH AI Anti Image (ASC) To 16 ch DAC DAC_1 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 16 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: IO_289 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 00 ; PORT ? | 16 CH AI To 16 ch DAC ; ?? Duplicate of 278 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 00 ; PORT ? | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: IO_290 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 00 ; PORT ? | 32 CH AA To 32 ch ADC ; ?? Duplicate of 276 (Use for extra LSC ADC2?) | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 00 ; PORT ? | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: IO_291 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 00 ; PORT ? | 32 CH AA To 32 ch ADC ; ?? Duplicate of 277 | C1 | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 00 ; PORT ? | SCSI-3 Cable, HPDB68 Male / HPDB68 Male, 2.0m | 6
CAB_L1: ISC_292 | IOT2L | DB25F | PICOMOTOR FLANGE | IOT2L PICOMOTOR FLANGE To D1100323 PICOMOTOR Controller #4 (ISCT2L/IOT1) | DB25M | IOT2L | Pcont #4; Channels 1-4 | DB25 | 10
CAB_L1: ISC_293 | IOT1 | DB25F | PICOMOTOR FLANGE | ISCT1 TABLE PICOMOTOR FLANGE To D1100323 PICOMOTOR Controller #4 (ISCT2L/IOT1) | DB25M | ISCT2L | Pcont #4; Channels 5-8 | DB25 | 50
CAB_L1: ISC_294 | IOT2L | DB15F | Shutter Control 1 Logic | IOT2L TABLE D1102312 Shutter Control 1 Logic To Beckhoff 5 (Male end in LVEA) | DB15M | C2 | 3; PORT A | DB15 | 147
CAB_L1: ISC_295 | ISCT1 | DB15F | Shutter Control 2 Logic | ISCT1 TABLE D1102312 Shutter Control 2 Logic To Beckhoff 5 (Male end in LVEA) | DB15M | C2 | 3; PORT B | DB15 | 147
CAB_L1: ISC_296 | ISCT1 | DB15F | Shutter Control 3 Logic | ISCT1 TABLE D1102312 Shutter Control 3 Logic To Beckhoff 5 (Male end in LVEA) | DB15M | C2 | 3; PORT C | DB15 | 147
CAB_L1: ISC_297 | IOT2L | DB9F | IMC Refi beam Flange | IOT2L IMC Refi beam Flange To D1102312 Shutter Control 1 | DB9M | IOT2L | Shutter Control 1 | DB9 | 10
CAB_L1: ISC_298 | ISCT1 | DB9F | PSL Beam Flange | ISCT1 TABLE PSL Beam beam Flange To D1102312 Shutter Control 2 | DB9M | ISCT1 | Shutter Control 2 | DB9 | 10
CAB_L1: ISC_299 | ISCT1 | DB9F | PSL Beam Flange | ISCT1 TABLE X & Y ALS Beam beam Flange To D1102312 Shutter Control 2 | DB9M | ISCT1 | Shutter Control 2 | DB9 | 10
CAB_L1: ISC_300 | ISCT1 | DB9F | PSL Beam Flange | ISCT1 TABLE POP Beam beam Flange To D1102312 Shutter Control 3 | DB9M | ISCT1 | Shutter Control 3 | DB9 | 10
CAB_L1: ISC_301 | ISCT1 | DB9F | PSL Beam Flange | ISCT1 TABLE REFL Beam beam Flange To D1102312 Shutter Control 3 | DB9M | ISCT1 | Shutter Control 3 | DB9 | 10
CAB_L1: ISC_302 | R5 | DB9M | 18 ; Analog out (4-7) | D1002559 ISC Whitening Chassis To 32 CH AA (LSC_ADC0-4) | C1 | DB9F | 9 ; LSC_ADC0_4 | DB9 | 127
CAB_L1: IO_303 | IOT2L | DB25M | Controller 5; PORT 1 (Readback) | D1100323 Picomotor Interface (#5) (HAM2) To D1100680 Beckhoff EtherCAT 2 (Picomotor, Serial Ports, Modbus) | C2 | DB25F | 15 ; PORT 2 (Readback) | DB25 | 142
CAB_L1: IO_304 | IOT2L | DB25F | Controller 5; PORT 1 (Controls) | D1100323 Picomotor Interface (#5) (HAM2) To D1100680 Beckhoff EtherCAT 2 (Picomotor, Serial Ports, Modbus) | C2 | DB25M | 15 ; PORT 2 (Control) | DB25 | 142
CAB_L1: IO_305 | SUS-R3 | DB25M | Controller 6; PORT 1 (Readback) | D1100323 Picomotor Interface (#6) (OL) To D1100680 Beckhoff EtherCAT 2 (Picomotor, Serial Ports, Modbus) | C2 | DB25F | 15 ; PORT 3 (Readback) | DB25 | 142
CAB_L1: IO_306 | SUS-R3 | DB25F | Controller 6; PORT 1 (Controls) | D1100323 Picomotor Interface (#6) (OL) To D1100680 Beckhoff EtherCAT 2 (Picomotor, Serial Ports, Modbus) | C2 | DB25M | 15 ; PORT 3 (Control) | DB25 | 142
CAB_L1: ISC_307 | HAM6 | DB25F | ASC_OMCR_A & B FLANGE D6-F1 | HAM6 OMC DCPD 1 & 2 Preamp To D1002559 ISC Whitening Chassis | R5 | DB25M | 18 ; CH 4-7 | DB25 | 25
CAB_L1: ISC_308 | IOT2L | DB9F | PSL Beam Flange | IOT2L TABLE PC_4 To Flange | IOT2L | DB9M | Patch Panel | DB9 | 6
CAB_L1: ISC_309 | ISCT1 | DB9F | PSL Beam Flange | ISCT1 TABLE PC_4 To Flange | ISCT1 | DB9M | Patch Panel | DB9 | 6
CAB_L1: ISC_310 | C3 | DB37M | 18; PORT CTRL | D1100262 Controls RF Amp_1 Concentrator To D1100681 EtherCAT Corner Station 3 | C2 | DB37F | 11 ; PORT 8 | DB37 | 20
CAB_L1: ISC_311 | C3 | DB37M | 16; PORT CTRL | D1100262 Controls RF Amp_2 Concentrator To D1100681 EtherCAT Corner Station 3 | C2 | DB37F | 11 ; PORT 9 | DB37 | 20
CAB_L1: ISC_312 | R4 | DB37M | 39; PORT CTRL A | D1100696 ASC Demod Concentrator 3-A To D1101266 Beckhoff EtherCAT 4-3 (ASC Demod) | C2 | DB37F | 6 ; PORT 3 | DB37 | 142
CAB_L1: ISC_313 | R4 | DB37M | 39; PORT CTRL B | D1100696 ASC Demod Concentrator 3-B To D1101266 Beckhoff EtherCAT 4-4 (ASC Demod) | C2 | DB37F | 6 ; PORT 4 | DB37 | 142
CAB_L1: ISC_314 | HAM1 | DB25F | D2-1C1 | REFL AIR BEAM DIVERTER To D1200132 Beckhoff EtherCAT 5 (Beam Diverters) | C2 | DB9M | 3; PORT E | DB25 | 130
CAB_L1: ISC_315 | HAM1 | DB25F | D2-1C2 | POP AIR BEAM DIVERTER To D1200132 Beckhoff EtherCAT 5 (Beam Diverters) | C2 | DB9M | 3; PORT F | DB25 | 130
CAB_L1: ISC_316 | HAM6 | DB25F | D6-F9 | OMC AIR BEAM DIVERTER To D1200132 Beckhoff EtherCAT 5 (Beam Diverters BDV2) | C2 | DB9M | 3; PORT G | DB25 | 130
CAB_L1: ISC_317 | HAM6 | DB25F | D6-F8 | AS AIR BEAM DIVERTER To D1200132 Beckhoff EtherCAT 5 (Beam Diverters BDV1) | C2 | DB9M | 3; PORT H | DB25 | 130
CAB_L1: ISC_318 | R4 | DB25F | 35 ; Controls | D1200136 ALS Fiber Distribution To To D1200132 Beckhoff EtherCAT 5 (ALS Fiber Distribution) | C2 | DB25M | 3; PORT 4 | DB25 | 147
CAB_L1: ISC_319 | R4 | DB37M | 17;Controls 1 | D1200148 Summing Module To D1200132 Beckhoff EtherCAT 5 Slot 2 (Controls1) | C2 | DB37F | 3; PORT 2 | DB37 | 142
CAB_L1: ISC_320 | R4 | DB37M | 17; Controls 2 | D1200148 Summing Module To D1200132 Beckhoff EtherCAT 5 Slot 3 (Controls2) | C2 | DB37F | 3; PORT 3 | DB37 | 142
CAB_L1: ISC_321 | R1 | DB25M | 30 ; Controls | D1002178 158.8Mhz ALS Frequency Doubler To D1100262 RF Amp Concentrator 2 | C3 | DB25F | 16 port 11 | DB25 | 145
CAB_L1: ISC_322 | R4 | DB25M | 36 ; Controls | D1002178 158.8Mhz PSL Frequency Doubler To D1100262 RF Amp Concentrator 2 | C3 | DB25F | 16 port 12 | DB25 | 145
CAB_L1: ISC_323 | ISCT6 | DB15 | Shutter Control 4 | ISCT6 TABLE D1102313 Shutter Control 4 To D1200132 Beckhoff Concentrator 5 | C2 | DB15 | 3; PORT D | DB25 | 129
CAB_L1: ISC_324 | R4 | DB25M | 31 ; To Whitening | D1002481 Dual QPD Amp (SM2 PSL) To D1002559 Whitening/VGA (SM2 PSL) | R4 | DB25F | 32 ; Analog Signal Input | DB25 | 6
CAB_L1: ISC_325 | ISCT6 | DB9F | Shutter Control 4 | ISCT6 AS beam Flange To D1102312 Shutter Control 4 | ISCT6 | DB9M | Shutter # 4 ; Shutter 1 | DB9 | 6
CAB_L1: ISC_326 | R4 | DB37M | 21; PORT CTRL | D1102065 Auxiliary Signals Concentrator 1 To D1200132 Beckhoff EtherCAT 5 Slot 10 (Aux ISCT1) | C2 | DB37F | 3; PORT 10 | DB37 | 142
CAB_L1: ISC_327 | R5 | DB37M | 16 ; PORT CTRL | D1102065 Auxiliary Signals Concentrator 1 To D1200132 Beckhoff EtherCAT 5 Slot 8 (Aux ISCT6) | C2 | DB37F | 3; PORT 8 (ISCT6 Auxillary) | DB37 | 129
CAB_L1: ISC_328 | R4 | DB37M | 20; PORT CTRL | D1201345 Auxiliary Signals Concentrator 3 To D1200132 Beckhoff EtherCAT 5 Slot 9 (DC PDs ISCT1) | C2 | DB37F | 3; PORT 9 | DB37 | 142
CAB_L1: ISC_329 | R5 | DB37M | 15 ; PORT CTRL | D1201345 Auxiliary Signals Concentrator 4 To D1200132 Beckhoff EtherCAT 5 Slot 7 (DC PDs ISCT6) | C2 | DB37F | 3; PORT 7 (DC PDs ISCT6) | DB37 | 129
CAB_L1: ISC_330 | ISCT1 | DB15F | TEC oven | ISCT1 TABLE TEC oven To ISCT1 feedthrough | ISCT1 | DB15M | Generic Interface | DB15 | 6
CAB_L1: ISC_331 | ISCT1 | DB15F | Generic Interface FLANGE | ISCT1 TABLE ISCT1 feedthrough to D1200132 Beckhoff ETherCAT5 Slot 11 (TEC Oven) | C2 | DB15M | 3; PORT 11 | DB15 | 147
CAB_L1: ISC_332 | R2 | DB25F | 36; PORT 2 | D0900128 9.099/8.684MHz Dual Delay Line To D1100681 EtherCAT Corner Station 3 | C2 | DB25M | 9; PORT 7 | DB25 | 145
CAB_L1: ISC_333 | C3 | DB9M | 11 ; RS422 | Timing Fanout D080534 to Serial Concentrator D1100632 | C2 | DB9F | 35; PORT 5 | DB9 | 6
CAB_L1: ISC_334 | SEI/SUS rack | DB9M |  | Timing Fanout D080534 to Serial Concentrator D1100632; only other timing fanout is in L1:FEC-C1, is this needed? | C2 | DB9F | 35; PORT 6 | DB9 | 50
CAB_L1: ISC_335 | C2 | DB37M | 35; Controls | Serial Concentrator D1100632 to EtherCAT Corner Station 2; was: Timing Fanout D080534 to Serial Concentrator D1100632 | C2 | DB37F | 15; PORT 12 | DB9 | 5
CAB_L1: ISC_336 | C2 | RJ-45 | 33; ECAT PORT 1 | D1100251 Binary IO Chassis 1 to D1100680 EtherCAT Corner Station 2 | C2 | RJ-45 | 15; PORT 1B | CAT5 | 5
CAB_L1: ISC_337 | C2 | RJ-45 | 31; ECAT PORT 1 | D1100251 Binary IO Chassis 2 to D1100251 Binary IO Chassis 1 | C2 | RJ-45 | 33; ECAT PORT 2 | CAT5 | 1
CAB_L1: ISC_338 | C2 | RJ-45 | 28; ECAT PORT 1 | D1100251 Binary IO Chassis 3 to D1100680 EtherCAT Corner Station 2 | C2 | RJ-45 | 15; PORT 2B | CAT5 | 5
CAB_L1: ISC_339 | C2 | RJ-45 | 26; ECAT PORT 1 | D1100251 Binary IO Chassis 4 to D1100251 Binary IO Chassis 1 | C2 | RJ-45 | 28; ECAT PORT 2 | CAT5 | 1
CAB_L1: ISC_340 | C2 | RJ-45 | 19; AUX PORT 1 | D1002961 EtherCAT Corner Station 1/ISC Common to D1100680 EtherCAT Corner Station 2 (CAT2) | C2 | RJ-45 | 15; PORT IN | CAT5 | 1
CAB_L1: ISC_341 | C2 | RJ-45 | 15; PORT OUT | D1100680 EtherCAT Corner Station 2 to D1100681 EtherCAT Corner Station 3 (CAT3) | C2 | RJ-45 | 11; PORT IN | CAT5 | 1
CAB_L1: ISC_342 | C2 | RJ-45 | 11; PORT OUT | D1100681 EtherCAT Corner Station 3 to D1101266 EtherCAT Corner Station 4 (CAT4) | C2 | RJ-45 | 7; PORT IN | CAT5 | 1
CAB_L1: ISC_343 | C2 | RJ-45 | 7; PORT OUT | D1101266 EtherCAT Corner Station 4 to D1200132 EtherCAT Corner Station 5 (CAT5) | C2 | RJ-45 | 3; PORT IN | CAT5 | 1
CAB_L1: ISC_400 | R5 | DB9M | 8 ; Analog Out (0-3) | D1002559 ISC Whitening (OMC-A QPD) To 32 CH AA Anti Aliasing (ASC_ADC6-4) | C1 | DB9F | 28 ; ASC_ADC6-4 | DB9F
CAB_L1: ISC_401 | R5 | DB9M | 8 ; Analog Out (4-7) | D1002559 ISC Whitening (OMC-B QPD) To 32 CH AA Anti Aliasing (ASC_ADC6-5) | C1 | DB9F | 28 ; ASC_ADC6-5 | DB9F
CAB_L1: ISC_402 | R5 | DB37F | 8 ; Board 1, From Binary Output Module | D1002559 ISC Whitening (OMC-A&B QPD) To D1100251 384 Channel Binary Output (BO4) Whitening; Chassis 3-1 | C2 | DB37M | 26 ; CHASSIS 3-1 | DB37
CAB_L1: ISC_403 | R5 | DB37F | 8 ; Board 2, From Binary Output Module | D1002559 ISC Whitening (OMC-A&B QPD) To D1100251 384 Channel Binary Output (BO4) Whitening ; CHASSIS 3-2 | C2 | DB37M | 26 ; CHASSIS 3-2
CAB_L1: ISC_404 | HAM6 | DB24 | D6-F3 | HAM6 OMC A & B QPD To D1002481 Dual QPD Transimpedance Amp | R5 | DB25 | 10 ; PD Input
CAB_L1: ISC_405 | R5 | DB25 | 10 ; To Whitening | D1002481 Dual QPD Transimpedance Amp (OMC-A, OMC-B QPD) To D1002559 Whitening | R5 | DB25 | 8 ; Analog Signal Input | DB25
CAB_L1: ISC_406 | R5 | DB9F | 12 ; DSUB 1 | DB9 Breakout Panel D1201450 to To 16 CH AI Anti Imaging (LSC_DAC0-1) | C1 | DB9F | 5 ; PORT 4 | DB9
CAB_L1: ISC_407 | R5 | DB9M | 12 ; DSUB 2 | DB9 Breakout Panel D1201450 to To 32 CH AA Anti Aliasing (ASC_ADC6-4) | C1 | DB9M | 9 ; PORT 5 | DB9
CAB_L1: ISC_409 | HAM6 | DB25 | D6-F2 | HAM6 flange to D1300485 PZT Driver | R5 | DB25 | 13 ; To OMC HV/LV Piezos | DB25
CAB_L1: ISC_410 | R5 | DB9M | 32 ; Analog Outputs to AA | D1102079 LSC RFPD Interface to 32 CH AA Anti Aliasing (LSC_ADC1-4) | C1 | DB9M | 8 ; port 4
CAB_L1: ISC_411 | C3 | DB37M | 14; PORT CTRL | D1100262 Controls RF Amp_3 Concentrator To D1300745 EtherCAT Corner Station 6 | C2 | DB37F | 23; PORT 11 | DB37 | 12
CAB_L1: ISC_412 | C4 | DB25M | 6;Controls | D1000124 79.2 MHz RF Distribution Amp To D1100262 Controls RF Amp_3 Concentrator | C3 | DB25F | 14; PORT 1 | DB25 | 12
CAB_L1: ISC_413 | R1 | DB25M | 36; Controls | D1000124 71 MHz RF Distribution Amp To D1100262 Controls RF Amp_3 Concentrator | C3 | DB25F | 14; PORT 2 | DB25 | 145
CAB_L1: ISC_414 | R1 | DB25M | 22-23; PLL | D090605 79.4MHz VCO (ALS COMM PLL) Low Noise VCO To D1300745 Beckhoff EtherCAT 6 | C2 | DB25F | 23 ; PORT 7 | DB25 | 147
CAB_L1: ISC_415 | R1 | DB25M | 22-23; Controls | D090605 79.4MHz VCO (ALS COMM FDD) Low Noise VCO To D1300745 Beckhoff EtherCAT 6 | C2 | DB25F | 23 ; PORT 8 | DB25 | 147
CAB_L1: ISC_416 | R1 | DB25M | 32-33; PLL | D090605 79.4MHz VCO (ALS DIFF PLL) Low Noise VCO To D1300745 Beckhoff EtherCAT 6 | C2 | DB25F | 23 ; PORT 9 | DB25 | 147
CAB_L1: ISC_417 | R1 | DB25M | 32-33; Controls | D090605 79.4MHz VCO (ALS DIFF FDD) Low Noise VCO To D1300745 Beckhoff EtherCAT 6 | C2 | DB25F | 23 ; PORT 10 | DB25 | 147
CAB_L1: ISC_418 | R1 | DB9M | 22-23; DAQ & 32-33; DAQ | D1300976 Y-cable From D090605 79.4MHz VCO (ALS COMM PLL) Low Noise VCO To 32 CH AA Anti Aliasing (LSC_ADC2-4) | C1 | DB9F | 6; IN 13-16 | DB9 | 149
CAB_L1: ISC_419 | R4 | DB9M | 17; DAQ Right | D1200148 Summing Module To 32 CH AA Anti Aliasing (LSC_ADC2-2) | C1 | DB9F | 6; IN 5-8 | DB9 | 144
CAB_L1: ISC_420 | R4 | DB9F | 18; DSUB 1 | DB9 Breakout Panel D1201450 To 32 CH AA Anti Aliasing (LSC_ADC2-3) | C1 | DB9F | 6; IN 9 -12 | DB9 | 144
CAB_L1: ISC_421 | R4 | DB9F | 18; DSUB 2 | DB9 Breakout Panel D1201450 To 16 CH AI Anti Imaging (LSC_DAC0-3) | C1 | DB9M | 5; OUT 9 - 12 | DB9 | 144
CAB_L1: ISC_422 | ISCT1 | DB9M | GENERIC INTERFACE FLANGE | D1002932 Generic Interface Flange To D1201345 EtherCAT Concentrator 3 (Photodode 1-4 IN/OUT) | R4 | DB9F | 20; PD DC 1-4 IN | DB9 | 40
CAB_L1: ISC_422 | ISCT6 | DB9M | GENERIC INTERFACE FLANGE | D1002932 Generic Interface Flange To D1201349 EtherCAT Concentrator 4 (Photodode 1-4 IN/OUT) | R5 | DB9F | 15; PD DC 1-4 IN | DB9 | 25
CAB_L1: ISC_423 | R5 | DB25M | Fast | Fast Shutter Controller To D1300745 EtherCAT Chassis 6 (Fast Shutter HAM6) | C2 | DB25F | 23 ; PORT 6 | DB9 | 129
CAB_L1: ISC_424 | R4 | DB9M | 37 ; DC Output Head 3 | D1101906 WFS RFPD Interface To 32 CH AA (ASC_ADC3), in-vac WFS | C1 | DB9F | 33 ; PORT 5 | DB9 | 144
CAB_L1: ISC_425 | R4 | DB9M | 37 ; DC Output Head 4 | D1101906 WFS RFPD Interface To 32 CH AA (ASC_ADC3), in-vac WFS | C1 | DB9F | 33 ; PORT 6 | DB9 | 144
CAB_L1: ISC_426 | R5 | DB9M | 30 ; DC Outputs Head 3 | D1101906 WFS RFPD Interface To 32 CH AA (ASC_ADC5), in-vac WFS | C1 | DB9F | 30 ; PORT 5 | DB9 | 127
CAB_L1: ISC_427 | R5 | DB9M | 30 ; DC Outputs Head 4 | D1101906 WFS RFPD Interface To 32 CH AA (ASC_ADC5), in-vac WFS | C1 | DB9F | 30 ; PORT 6 | DB9 | 127
CAB_L1: ISC_428 | R4 | DB9M | 20 ; PD Amp Out 1-4 | D1201345 Aux concentrator 3 To 32 CH AA (ASC_ADC3), ALS green PDs | C1 | DB9F | 33 ; PORT 7 | DB9 | 144
CAB_L1: ISC_430 | PSL | DB9M | Port labeled DAQ, H1 PSL enclosure | D0900760 EOM Driver 9 MHz To 32 CH AA Anti Aliasing | C1 | DB9F | 6 ; 17-20 | DB9 | 175
CAB_L1: ISC_431 | PSL | DB9M | Port labeled DAQ, H1 PSL enclosure | D0900760 EOM Driver 45 MHz To 32 CH AA Anti Aliasing | C1 | DB9F | 6 ; 21-24 | DB9 | 175
CAB_L1: ISC_432 | PSL | DB925M | Port labeled Controls, H1 PSL enclosure | D0900760 EOM Driver 9MHz To D1300745 Beckhoff EtherCAT 6 | C2 | DB25F | 23 ; PORT 4 | DB9 | 175
CAB_L1: ISC_433 | PSL | DB925M | Port labeled Controls, H1 PSL enclosure | D0900760 EOM Driver 45MHz To D1300745 Beckhoff EtherCAT 6 | C2 | DB25F | 23 ; PORT 5 | DB9 | 175